e-PU Cabinet V2

Measurement Plan

Requirements Verification Plan

Based on: e-PU cabinet V2 project plan (2).docx

Version: 2.0

Date: 2026-07-08

# Introduction

This document is the Measurement Plan for the e-PU Cabinet V2 project a low-cost, high performance stationary Battery Energy Storage System (BESS) that uses Solar East cabinet hardware together with VDL Energy Systems control software.

Purpose: to make sure every requirement from the project plan is verified during the test phase, with nothing missed.

This plan follows the standard verification approach (Verification Cross-Reference Matrix + test sheets). It is split into two easy-to-use parts:

- Section 3

  - Verification Cross-Reference Matrix: a short, at-a-glance list of every requirement with its verification method and status. Use this to see overall progress.

- Section 4

  - Test Sheets: one small card per requirement with the exact test steps, pass criteria and equipment. Use this while performing each test.

## How to use this plan

Work through the Test Sheets (Section 4) one requirement at a time.

For each test sheet, follow "How to test", then write the measured value in "Result".

Set the Status to Pass or Fail based on the acceptance criterion.

Copy the Pass/Fail result back into the matrix (Section 3) to track overall progress.

Confirm the Coverage Checklist (Section 5), then complete Sign-off (Section 7).

# Legend

## Verification methods

| Code | Method | What it means |
| --- | --- | --- |
| T | Test | Physically operate and measure it with instruments. |
| I | Inspection | Look at it - visual check, dimensions, or document/certificate review. |
| A | Analysis | Calculation, simulation, or engineering analysis (e.g. efficiency, FEM). |
| D | Demonstration | Show it works under normal operation, without dedicated measurement. |

## Status values

| Status | Meaning |
| --- | --- |
| Not started | Test not performed yet. |
| In progress | Test currently being executed. |
| Pass | Verified - acceptance criterion met. |
| Fail | Acceptance criterion not met - corrective action required. |

# Verification Cross-Reference Matrix

At-a-glance list of every requirement. Full test details are in Section 4 (Test Sheets). Fill in the Status column as testing progresses.

| ID | Requirement | Method | Test stage | Status |
| --- | --- | --- | --- | --- |
| SAFE-006 | Battery cell safety (UN38.3 / IEC 62619) | I | TRL 2 |  |
| SAFE-007 | Power electronics (IEC 62477) | I | TRL 2 |  |
| COST-001 | Controller material cost < EUR 3500 | A | TRL 2 |  |
| COMM-001 | Modbus TCP | T | TRL 3 |  |
| COMM-002 | CAN bus | T | TRL 3 |  |
| COMM-003 | Ethernet | T | TRL 3 |  |
| COMM-004 | RS485 | T | TRL 3 |  |
| MECH-001 | Cabinet dimensions 1000x2300x1350 mm | I | TRL 3 |  |
| MECH-002 | Cabinet weight <= 2450 kg | I / A | TRL 3 |  |
| ELEC-001 | Rated AC output power 125 kW | T | TRL 4 |  |
| ELEC-004 | DC voltage 832 V nominal (702-936 V range) | T | TRL 4 |  |
| ELEC-005 | AC voltage 400 V (+-15% grid / +-3% island) | T | TRL 4 |  |
| ELEC-006 | Grid frequency 50/60 Hz | T | TRL 4 |  |
| ELEC-010 | Grid response time < 100 ms | T | TRL 4 |  |
| FUNC-001 | Grid-following operation | T / D | TRL 4 |  |
| FUNC-002 | Grid-forming (island) operation | T / D | TRL 4 |  |
| ELEC-002 | Peak power 110% continuous / 120% for 1 min | T | TRL 5 |  |
| ELEC-003 | Usable capacity >= 250 kWh at SOH 99% | T | TRL 5 |  |
| ELEC-007 | THD < 3% with linear load | T | TRL 5 |  |
| ELEC-008 | Power factor range -1 to +1 | T | TRL 5 |  |
| ELEC-009 | Round-trip efficiency > 88% | A / T | TRL 5 |  |
| FUNC-003 | Multi-BESS parallel up to 1 MW | T | TRL 5-6 |  |
| FUNC-004 | Peak shaving / load management | D | TRL 5-6 |  |
| FUNC-009 | Microgrid load sharing | T | TRL 5-6 |  |
| FUNC-010 | Redundancy / fail-safe | D | TRL 5-6 |  |
| THERM-001 | Operating temp -20 to +55 C | T / A | TRL 5-6 |  |
| THERM-002 | Noise < 75 dB(A) at 1 m | T | TRL 5-6 |  |
| SAFE-003 | Overcurrent protection | T | TRL 5 |  |
| SAFE-004 | Overvoltage protection | T | TRL 5 |  |
| SAFE-008 | Safe state on fault / island | T / D | TRL 5-6 |  |
| MECH-003 | IP54 ingress protection | I / T | TRL 6 |  |
| FUNC-005 | PV control and curtailment | D / T | TRL 6 |  |
| FUNC-006 | Generator control (fixed power) | D | TRL 6 |  |
| FUNC-007 | Black start capability | D / T | TRL 6 |  |
| FUNC-008 | Automatic mains failure recovery | D / T | TRL 6 |  |
| FUNC-011 | HMI / service portal | D | TRL 6 |  |
| SAFE-001 | CE marking | I / A | TRL 6 |  |
| SAFE-002 | PGS 37-1 compliance | I / A | TRL 6 |  |
| SAFE-005 | EMC (IEC 61000) | I / T | TRL 6 |  |
| FUNC-012 | Uptime >= 98% | A | TRL 7 |  |

# Test Sheets

One card per requirement. Follow "How to test", record the "Result", then mark Pass or Fail.

## TRL 2

SAFE-006 - Battery cell safety (UN38.3 / IEC 62619)

| Requirement | LFP cells comply with UN38.3 (transport) and IEC 62619 (stationary storage safety). |
| --- | --- |
| Source | Hardware datasheet compliance standard |
| Verification method | I |
| How to test | Verify manufacturer UN38.3 and IEC 62619 certificates are available and valid for the LFP 314 Ah cells. |
| Acceptance criterion (pass condition) | Valid UN38.3 and IEC 62619 certificates on file. |
| Equipment / tooling | Manufacturer certificates |
| Test stage | TRL 2 / 3 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

SAFE-007 - Power electronics (IEC 62477)

| Requirement | The power electronics comply with IEC 62477. |
| --- | --- |
| Source | Hardware datasheet compliance standard |
| Verification method | I |
| How to test | Verify the manufacturer's IEC 62477 test report is available and valid for the inverter/power electronics. |
| Acceptance criterion (pass condition) | Valid IEC 62477 test report on file. |
| Equipment / tooling | Manufacturer test report |
| Test stage | TRL 2 / 3 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

COST-001 - Controller material cost < EUR 3500

| Requirement | Additional VDL controller hardware material cost is below EUR 3500 per system. |
| --- | --- |
| Source | Project plan - Cost/Budget section |
| Verification method | A |
| How to test | Sum the BOM cost of all VDL-added controller hardware (excluding the base Solar East cabinet) and compare to the EUR 3500 target. |
| Acceptance criterion (pass condition) | Total VDL controller BOM cost <= EUR 3500 per system. |
| Equipment / tooling | Bill of Materials, supplier quotations |
| Test stage | TRL 2 / 3 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

## TRL 3

COMM-001 - Modbus TCP

| Requirement | Modbus TCP communication is functional. |
| --- | --- |
| Source | System Requirements table |
| Verification method | T |
| How to test | Connect an RADZIO and read/write all defined Modbus registers over TCP/IP. |
| Acceptance criterion (pass condition) | All registers readable/writable; correct values; no errors |
| Equipment / tooling | Modbus TCP client (e.g. Modscan), network switch, PC |
| Test stage | TRL 3 / 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

COMM-002 - CAN bus

| Requirement | CAN bus communication is functional. |
| --- | --- |
| Source | System Requirements table; Hardware datasheet |
| Verification method | T |
| How to test | Connect a CAN analyser and verify frames between BMS, inverter and VDL controller. |
| Acceptance criterion (pass condition) | All defined CAN messages present; correct data; no lost frames |
| Equipment / tooling | CAN analyser (e.g. PCAN/Vector), CAN interface cable |
| Test stage | TRL 3 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

COMM-003 - Ethernet

| Requirement | Ethernet communication is functional. |
| --- | --- |
| Source | System Requirements table; Hardware datasheet |
| Verification method | T |
| How to test | Ping all networked devices and run full data exchange (HMI, controller, BMS, monitoring). |
| Acceptance criterion (pass condition) | All devices reachable; data exchange successful; latency < 50 ms. (Assumption.) |
| Equipment / tooling | Network switch, PC, ping/traceroute tools |
| Test stage | TRL 3 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

COMM-004 - RS485

| Requirement | RS485 communication is functional. |
| --- | --- |
| Source | Hardware datasheet |
| Verification method | T |
| How to test | Connect an RS485 device and verify data exchange using the defined protocol (Modbus RTU or similar). |
| Acceptance criterion (pass condition) | RS485 exchange successful; correct register values; no framing errors. |
| Equipment / tooling | RS485 USB adapter, Modbus RTU client |
| Test stage | TRL 3 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

MECH-001 - Cabinet dimensions 1000x2300x1350 mm

| Requirement | Cabinet dimensions are 1000 (W) x 2300 (H) x 1350 (D) mm. |
| --- | --- |
| Source | Hardware datasheet |
| Verification method | I |
| How to test | Measure width, height and depth of the assembled cabinet. |
| Acceptance criterion (pass condition) | W 1000 +-50 mm; H 2300 +-50 mm; D 1350 +-50 mm. |
| Equipment / tooling | Steel tape measure |
| Test stage | TRL 3 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

MECH-002 - Cabinet weight <= 2450 kg

| Requirement | Cabinet weight does not exceed 2450 kg. |
| --- | --- |
| Source | Hardware datasheet |
| Verification method | I / A |
| How to test | Verify weight from shipping documentation or weigh on a calibrated floor scale. |
| Acceptance criterion (pass condition) | Documented or measured weight <= 2450 kg. |
| Equipment / tooling | Calibrated industrial scale or supplier weight certificate |
| Test stage | TRL 3 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

## TRL 4

ELEC-001 - Rated AC output power 125 kW

| Requirement | The system delivers a rated AC output power of 125 kW. |
| --- | --- |
| Source | System Requirements table; Hardware datasheet |
| Verification method | T |
| How to test | Connect a rated load. Measure AC output power with a power analyser at rated conditions. |
| Acceptance criterion (pass condition) | Measured output power >= 125 kW at 400 V AC, 50 Hz. |
| Equipment / tooling | Power analyser calibrated |
| Test stage | TRL 4 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

ELEC-004 - DC voltage 832 V nominal (702-936 V range)

| Requirement | DC bus operates at 832 V nominal within a 702-936 V range. |
| --- | --- |
| Source | Hardware datasheet |
| Verification method | T |
| How to test | Monitor DC bus voltage during a full charge/discharge cycle. |
| Acceptance criterion (pass condition) | DC bus voltage stays within 702-936 V throughout; nominal ~832 V. |
| Equipment / tooling | Calibrated DC voltmeter / data logger on DC bus |
| Test stage | TRL 4 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

ELEC-005 - AC voltage 400 V (+-15% grid / +-3% island)

| Requirement | AC output is 400 V, +-15% on-grid and +-3% off-grid (island). |
| --- | --- |
| Source | Hardware datasheet |
| Verification method | T |
| How to test | Measure AC output voltage in grid-following and grid-forming modes under varying loads. |
| Acceptance criterion (pass condition) | Grid-following: 400 V +-15% (340-460 V); island: 400 V +-3% (388-412 V). |
| Equipment / tooling | True-RMS voltmeter / power analyser |
| Test stage | TRL 4 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

ELEC-006 - Grid frequency 50/60 Hz

| Requirement | The system supports both 50 Hz and 60 Hz grid frequencies. |
| --- | --- |
| Source | System Requirements table; Hardware datasheet |
| Verification method | T |
| How to test | Switch configuration between 50 Hz and 60 Hz. Verify output frequency in each mode. |
| Acceptance criterion (pass condition) | 50.00 +-0.5 Hz (50 Hz mode); 60.00 +-0.5 Hz (60 Hz mode). |
| Equipment / tooling | Frequency meter / power analyser |
| Test stage | TRL 4 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

ELEC-010 - Grid response time < 100 ms

| Requirement | The system responds to a power command within 100 ms. |
| --- | --- |
| Source | System Requirements table |
| Verification method | T |
| How to test | Send a step command (0 -> 100% setpoint) and timestamp the start and end of the power ramp. |
| Acceptance criterion (pass condition) | Time until response system < 100 ms. |
| Equipment / tooling | Oscilloscope or data logger (>= 1 ms resolution), power analyser |
| Test stage | TRL 4 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

FUNC-001 - Grid-following operation

| Requirement | The system follows grid voltage/frequency and injects/absorbs P and Q on command. |
| --- | --- |
| Source | Project scope; Objectives |
| Verification method | T / D |
| How to test | Connect to a simulated or live grid. Command P and Q setpoints and verify tracking. |
| Acceptance criterion (pass condition) | P within +-5% of command; Q within +-5 kVAr; stable for >= 5 min. |
| Equipment / tooling | Power analyser, grid simulator or live grid connection |
| Test stage | TRL 4 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

FUNC-002 - Grid-forming (island) operation

| Requirement | The system forms its own AC voltage/frequency in island/microgrid mode. |
| --- | --- |
| Source | Project scope; Objectives |
| Verification method | T / D |
| How to test | Disconnect from the grid (island mode), connect a local load, verify stable voltage/frequency without external reference. |
| Acceptance criterion (pass condition) | Stable island 400 V +-3%, 50 Hz +-0.5 Hz with load steps applied. |
| Equipment / tooling | Power analyser, programmable load bank, oscilloscope |
| Test stage | TRL 4 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

## TRL 5

ELEC-002 - Peak power 110% continuous / 120% for 1 min

| Requirement | The system sustains 110% power continuously and 120% power for 1 minute. |
| --- | --- |
| Source | System Requirements table |
| Verification method | T |
| How to test | Run at 110% rated power for >= 5 min, then at 120% rated power for exactly 1 min. Log power and temperature. |
| Acceptance criterion (pass condition) | 110% (137.5 kW) sustained without trip/derating; 120% (150 kW) held for 1 min without trip. |
| Equipment / tooling | Power analyser, thermal camera, data logger |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

ELEC-003 - Usable capacity >= 250 kWh at SOH 99%

| Requirement | The system provides at least 250 kWh usable energy at 99% state of health. |
| --- | --- |
| Source | System Requirements table |
| Verification method | T |
| How to test | Fully charge from 0% SOC, then discharge at rated power and measure total energy delivered. |
| Acceptance criterion (pass condition) | Discharged energy >= 250 kWh when battery SOH >= 99%. |
| Equipment / tooling | Power analyser, energy meter, BMS readout |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

ELEC-007 - THD < 3% with linear load

| Requirement | Total harmonic distortion is below 3% with a linear load. |
| --- | --- |
| Source | System Requirements table; Hardware datasheet |
| Verification method | T |
| How to test | Measure THD of AC output voltage and current at rated load with a linear (resistive) load. |
| Acceptance criterion (pass condition) | THD voltage < 3% and THD current < 3% at rated linear load. |
| Equipment / tooling | Power quality analyser with THD capability |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

ELEC-008 - Power factor range -1 to +1

| Requirement | The system operates across the full power factor range -1 to +1. |
| --- | --- |
| Source | Hardware datasheet |
| Verification method | T |
| How to test | Command leading, lagging and unity power factor at rated power. Record P and Q. |
| Acceptance criterion (pass condition) | Power factor controllable across -1.0 to +1.0 without fault. |
| Equipment / tooling | Power analyser with reactive power measurement |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

ELEC-009 - Round-trip efficiency > 88%

| Requirement | System round-trip efficiency is greater than 88%. |
| --- | --- |
| Source | System Requirements table |
| Verification method | A / T |
| How to test | Measure charge energy (E_charge) and discharge energy (E_discharge). Compute efficiency = E_discharge / E_charge x 100%. |
| Acceptance criterion (pass condition) | Calculated round-trip efficiency >= 88%. |
| Equipment / tooling | Energy meters on AC input and output, data logger |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

FUNC-003 - Multi-BESS parallel up to 1 MW

| Requirement | Multiple cabinets operate in parallel up to 1 MW total power. |
| --- | --- |
| Source | System Requirements table; Objectives |
| Verification method | T |
| How to test | Connect >= 2 cabinets in parallel; verify load sharing and combined output |
| Acceptance criterion (pass condition) | Each unit shares load within +-10% of expected share; combined output reaches command without instability. |
| Equipment / tooling | Power analyser per unit, master controller, comms network |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

FUNC-004 - Peak shaving / load management

| Requirement | The system reduces grid peak demand to a configured setpoint on command. |
| --- | --- |
| Source | Project scope |
| Verification method | D |
| How to test | Configure a peak-shaving setpoint, apply a step-load above it, verify the system limits grid import. |
| Acceptance criterion (pass condition) | Grid import does not exceed setpoint +-5 kW within 100 ms of load step. |
| Equipment / tooling | Power analyser at grid connection, programmable load |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

FUNC-009 - Microgrid load sharing

| Requirement | Multiple BESS units share load automatically in a microgrid. |
| --- | --- |
| Source | Objectives; Deliverables |
| Verification method | T |
| How to test | Run >= 2 units in an island microgrid, apply variable loads, verify automatic load sharing. |
| Acceptance criterion (pass condition) | Load-sharing deviation <= +-10% of each unit's rated power; no instability over a 10-min test. |
| Equipment / tooling | Power analysers per unit, load, controller |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

FUNC-010 - Redundancy / fail-safe

| Requirement | A single unit failure does not cause complete system shutdown. |
| --- | --- |
| Source | Objectives; Deliverables |
| Verification method | D |
| How to test | In a multi-BESS setup, force one unit offline (simulate fault); verify remaining units keep supplying load. |
| Acceptance criterion (pass condition) | Remaining units take over load within 10 s; system stays operational; alarms raised correctly. |
| Equipment / tooling | Controller logs, power analysers |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

THERM-001 - Operating temp -20 to +55 C

| Requirement | The system operates from -20 C to +55 C. |
| --- | --- |
| Source | System Requirements table; Hardware datasheet |
| Verification method | T / A |
| How to test | verify via manufacturer thermal data and cooling-design analysis. |
| Acceptance criterion (pass condition) | Keeps working as intended at temperatures below 55 and above -20. |
| Equipment / tooling | thermal camera, data logger; or thermal datasheet |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

THERM-002 - Noise < 75 dB(A) at 1 m

| Requirement | Acoustic noise is below 75 dB(A) at 1 m. |
| --- | --- |
| Source | System Requirements table |
| Verification method | T |
| How to test | Measure A-weighted sound pressure level at 1 m from each cabinet face during full-load operation. |
| Acceptance criterion (pass condition) | Maximum measured noise < 75 dB(A) at 1 m under full load. |
| Equipment / tooling | Calibrated sound level meter |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

SAFE-003 - Overcurrent protection

| Requirement | The system disconnects safely on AC or DC overcurrent. |
| --- | --- |
| Source | Project plan (Risk - protection testing) |
| Verification method | T |
| How to test | Inject an overcurrent condition (load bank or simulated fault) and verify protection trips within the specified time. <= 100 ms |
| Acceptance criterion (pass condition) | Trips within <= 100 ms; no permanent damage; alarms raised; restart possible after fault clearance. |
| Equipment / tooling | Load bank / fault injection setup, oscilloscope, data logger |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

SAFE-004 - Overvoltage protection

| Requirement | The system disconnects safely on AC or DC overvoltage. |
| --- | --- |
| Source | Project plan (Risk - overvoltage validation) |
| Verification method | T |
| How to test | Apply an overvoltage condition above the defined threshold and verify protection trips within the specified time <= 100 ms. |
| Acceptance criterion (pass condition) | Trips within the specified time; no permanent damage; alarms raised. |
| Equipment / tooling | Programmable AC/DC source or field injection, oscilloscope |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

SAFE-008 - Safe state on fault / island

| Requirement | The system enters a defined safe state on fault detection. |
| --- | --- |
| Source | Project scope |
| Verification method | T / D |
| How to test | Simulate fault conditions (grid loss, comms loss, BMS fault) and verify the correct protective action (safe shutdown, island mode, alarms). |
| Acceptance criterion (pass condition) | Correct safe state for each fault within the specified time; <10 s no uncontrolled energy release; alarms correct. |
| Equipment / tooling | Fault simulation tools, controller logs, power analysers |
| Test stage | TRL 5 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

## TRL 6

MECH-003 - IP54 ingress protection

| Requirement | The enclosure meets IP54 ingress protection. |
| --- | --- |
| Source | System Requirements table; Hardware datasheet |
| Verification method | I / T |
| How to test | Inspect seals/enclosure and verify the IP54 certificate. |
| Acceptance criterion (pass condition) | IP54 confirmed by certificate |
| Equipment / tooling | IP54 certificate |
| Test stage | TRL 6 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

THERM-003 - Aerosol fire protection

| Requirement | The aerosol fire suppression system is installed and functional. |
| --- | --- |
| Source | Hardware datasheet |
| Verification method | I / D |
| How to test | Inspect aerosol units for correct installation, expiry date and activation wiring; functional-test the activation signal. |
| Acceptance criterion (pass condition) | Units installed per layout; within service life; activation signal test succeeds. |
| Equipment / tooling | Inspection checklist, supplier activation-test procedure |
| Test stage | TRL 6 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

FUNC-005 - PV control and curtailment

| Requirement | The system integrates with a PV source and can curtail PV output. |
| --- | --- |
| Source | Objectives; Deliverables |
| Verification method | D / T |
| How to test | Connect a PV simulator, issue a curtailment command, measure PV power before and after. |
| Acceptance criterion (pass condition) | PV power curtailed to setpoint +-5% within 500 ms of command. |
| Equipment / tooling | PV simulator with power measurement, controller interface |
| Test stage | TRL 6 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

FUNC-006 - Generator control (fixed power)

| Requirement | The system coordinates with a generator at a fixed power setpoint. |
| --- | --- |
| Source | Objectives; Deliverables |
| Verification method | D |
| How to test | Connect a generator/simulator; verify the system accepts fixed generator power and adjusts BESS to compensate load variation. |
| Acceptance criterion (pass condition) | Generator power within +-5% of setpoint; BESS compensates smoothly without generator trip. |
| Equipment / tooling | Generator or simulator, power analysers, controller |
| Test stage | TRL 6 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

FUNC-007 - Black start capability

| Requirement | The system can start from zero and energise a dead microgrid. |
| --- | --- |
| Source | Objectives; Deliverables |
| Verification method | D / T |
| How to test | With grid disconnected and load de-energised, initiate the black-start sequence from the controller. |
| Acceptance criterion (pass condition) | Forms AC (400 V +-3%, 50 Hz +-0.5 Hz) from dead bus and energises load within 60 s |
| Equipment / tooling | Oscilloscope, power analyser, stopwatch/data logger |
| Test stage | TRL 6 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

FUNC-008 - Automatic mains failure recovery

| Requirement | The system detects grid loss and automatically switches to island mode. |
| --- | --- |
| Source | Deliverables |
| Verification method | D / T |
| How to test | Simulate a grid outage while in grid-following mode; verify automatic transfer to island/grid-forming mode. |
| Acceptance criterion (pass condition) | Transfer completed without load interruption > 100 ms; stable in island mode. |
| Equipment / tooling | Power analyser, oscilloscope on load side, data logger |
| Test stage | TRL 6 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

FUNC-011 - HMI / service portal

| Requirement | Monitoring and diagnostics are accessible via a web/local interface. |
| --- | --- |
| Source | Deliverables |
| Verification method | D |
| How to test | Open the service portal/HMI and verify real-time display of SOC, power, voltage, frequency, alarms, and manual setpoints. |
| Acceptance criterion (pass condition) | All parameters visible and updating live; a manual setpoint command reflected on the system within 5 s. |
| Equipment / tooling | PC/tablet with browser/HMI software, network connection |
| Test stage | TRL 6 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

SAFE-001 - CE marking

| Requirement | The system complies with applicable EU directives for CE marking. |
| --- | --- |
| Source | Objectives; Deliverables |
| Verification method | I / A |
| How to test | Review the CE technical file; verify all applicable directives are addressed with test reports (notified body or self-declaration). |
| Acceptance criterion (pass condition) | Valid CE Declaration of Conformity issued; technical file complete; all applicable directives addressed. |
| Equipment / tooling | CE technical file, notified body test reports |
| Test stage | TRL 6 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

SAFE-002 - PGS 37-1 compliance

| Requirement | The system complies with the Dutch PGS 37-1 guideline for stationary battery systems. |
| --- | --- |
| Source | Objectives; Deliverables |
| Verification method | I / A |
| How to test | Review the PGS 37-1 checklist against the design; verify installation, fire safety, ventilation and electrical-safety paragraphs. |
| Acceptance criterion (pass condition) | PGS 37-1 documentation complete; no open deviations without approved mitigation. |
| Equipment / tooling | PGS 37-1 document, compliance checklist, safety engineer review |
| Test stage | TRL 6 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

SAFE-005 - EMC (IEC 61000)

| Requirement | The system complies with the IEC 61000 series for EMC emissions and immunity. |
| --- | --- |
| Source | Hardware datasheet; Project plan (Risk - EMC) |
| Verification method | I / T |
| How to test | Review EMC test reports |
| Acceptance criterion (pass condition) | All applicable IEC 61000 parts passed; documented in the CE technical file. |
| Equipment / tooling | EMC test reports from manufacturer or accredited lab |
| Test stage | TRL 6 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

## TRL 7

FUNC-012 - Uptime >= 98%

| Requirement | System uptime is at least 98% in operational deployment. |
| --- | --- |
| Source | System Requirements table; TRL 7 |
| Verification method | A |
| How to test | Record total operating time and unplanned downtime over a pilot period (>= 30 days). Compute uptime = (total - downtime) / total x 100%. |
| Acceptance criterion (pass condition) | Uptime >= 98% over the measurement period. |
| Equipment / tooling | Data logger, controller uptime log, maintenance records |
| Test stage | TRL 7 |
| Result (fill in during testing) |  |
| Status (Pass / Fail) |  |

# Test Phase Overview

Testing follows the TRL (Technology Readiness Level) phases from the project plan. Each stage builds on the previous one and ends with a tollgate review.

| Stage | TRL | What is tested |
| --- | --- | --- |
| 1 - Design & Incoming Inspection | TRL 1-2 | Document/certificate review, dimensional check, BOM cost check |
| 2 - Controller Integration | TRL 3 | Comms buses, fire protection, initial checks |
| 3 - Stable Grid Control | TRL 4 | Grid following/forming, voltage/frequency, response time |
| 4 - Performance Validation | TRL 5 | Power, capacity, efficiency, THD, protection, redundancy |
| 5 - Field Readiness | TRL 6 | PV/generator, microgrid, black start, AMF, HMI, CE/PGS, IP, EMC |
| 6 - Pilot & Reliability | TRL 7 | Uptime monitoring, reliability, customer feedback |

# Sign-off

Complete this table when testing for a stage or the full campaign is finished.

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Tester / Test Engineer |  |  |  |
| Test Lead / Project Lead |  |  |  |
| Quality / Safety Engineer |  |  |  |
| Approver |  |  |  |

Declaration: all requirements in this plan have been verified. Results are recorded in the Test Sheets (Section 4). Any failures or open items are tracked in the project action system (GitHub).

Note: requirements marked "(Assumption)" contain an interpretation of a requirement not explicitly quantified in the source project plan and should be confirmed by the project team before testing.