# 3 BESS Wolong – Test Plan

Structured and optimized commissioning / factory acceptance test plan for the 3-unit Battery Energy Storage System (BESS) under PLC control.

## System Configuration

Number of BESS Units: 3

Power Rating per Unit: 100 kW

Energy Capacity per Unit: 241 kWh

Total Rated Power: 300 kW

Total Energy: 723 kWh

Controller: PLC

Operating Modes: Manual Power, Automatic Power Sharing, Peak Shaving, Curtailment, Idle Charging, SOC Target Charging.

# General Prerequisites, Safety & Acceptance Criteria

## Prerequisites (verify before starting any section)

Single-line diagram, protection settings and PLC parameter list reviewed and released.

All power and communication cabling verified; insulation / continuity checks passed.

Emergency Stop circuit tested and functional before energizing the DC side.

Firmware / software versions of PLC, PCS and BMS recorded on the cover sheet.

Metering (grid meter, unit power meters) calibrated and scaling verified.

Initial SOC of each unit recorded; SOC limits (min 20% / max 100%) configured.

Configured ramp rate, response time and Peak Shaving limits documented.

Test instruments (clamp meter / power analyzer) available for ±2% verification.

## Safety Checks

Confirm PPE (arc-flash rated) and lock-out / tag-out procedure in place.

Verify Emergency Stop is within reach and functional before each energized test.

Confirm battery contactors open on Disable / E-Stop before touching DC terminals.

Monitor cell/module temperature and DC voltage during charge and discharge sweeps.

Stop testing immediately on any protection trip, smoke, or abnormal noise/heat.

## Acceptance Criteria

Measured active power per unit within ±2% of the expected setpoint.

Grid import/export held at or below the configured Peak Shaving limit when capacity allows.

All protection functions (SOC, overload, E-Stop, communication loss) behave as specified.

No unexpected alarms, oscillation (hunting) or PCS trips during any test.

Every table row marked Pass (or Yes) with reviewer sign-off; failures logged with a corrective action and re-tested.

## How to Use the Tables

Each section below is a self-contained test table. Execute rows top-to-bottom; grouped incremental steps (e.g. discharge / charge / load sweeps) are performed consecutively without returning to zero between steps to save time. Record the outcome in the Approved column (Pass/Fail or Yes/No) and note any deviation in Comments.

# Section 1 – PLC Control & Basic Functional Tests

Objective: verify PLC start-up, communications, controlled shutdown and safety interlocks before any power dispatch tests.

| Test Name | Expected Results | Approved (Pass/Fail) | Comments |
| --- | --- | --- | --- |
| 1.1 PLC & Units Start-up Power on the system (3 units); confirm PLC boot and communication with all 3 units and the grid power meter. | PLC enters RUN mode with no faults. Communication established with all three units and the grid meter; all devices report Healthy. All three units become READY; no alarms; system available for operation. |  |  |
| 1.2 Grid Meter Communication Loss & Recovery Disconnect the grid meter, then reconnect it. | On disconnect: PLC detects the communication failure, generates an alarm and enters the configured fallback mode. On reconnect: normal operation resumes automatically. |  |  |
| 1.3 Disable Individual Unit Disable Unit 2 while Units 1 and 3 remain enabled. | Unit 2 shuts down safely; Units 1 and 3 remain online; PLC updates the available capacity accordingly. |  |  |
| 1.4 Disable Complete System Issue the Disable command to the whole system. | All units stop; battery contactors open; system enters Standby. |  |  |
| 1.5 Emergency Stop & Restart Activate Emergency Stop, then reset the E-Stop and re-enable the system. | On E-Stop: all PCS stop immediately, battery isolated, alarm generated, manual reset required. After reset & enable: PLC clears the alarm, all three units restart normally and the system returns to READY. |  |  |

# Section 2 – Manual Power Mode Tests

Mode: Manual Power Control. The PLC directly controls total BESS active power and distributes it equally between available units unless limited by unit availability or protection functions. Positive = discharge, negative = charge.

Prerequisite: all three units enabled, Peak Shaving disabled, SOC within limits.

| Test Name | Expected Results | Approved (Pass/Fail) | Comments |
| --- | --- | --- | --- |
| 2.1 Manual Mode Selection Enable all three units, select Manual Mode, verify Peak Shaving is disabled. | Manual Mode active; Peak Shaving disabled; power setpoint accepted; System Ready indication active. |  |  |
| 2.2 Zero Power Command Set manual power command = 0 kW. | Total BESS power = 0 kW; BESS remains online; no charging or discharging; no alarms. |  |  |
| 2.3 Incremental Discharge Sweep (grouped) Without returning to zero, step the manual discharge command through: 30 → 60 → 90 → 150 → 240 → 300 kW. | Power is shared equally across the three units at each step, actual power within ±2%, output stable: - 30 kW: 10 / 10 / 10 kW - 60 kW: 20 / 20 / 20 kW - 90 kW: 30 / 30 / 30 kW - 150 kW: 50 / 50 / 50 kW - 240 kW: 80 / 80 / 80 kW - 300 kW: 100 / 100 / 100 kW (all units at rated power, no overload alarms, stable). |  |  |
| 2.4 Maximum Discharge Limit Set manual power = 350 kW. | PLC limits total command to 300 kW; no unit exceeds 100 kW; warning/event logged (if configured). |  |  |
| 2.5 Incremental Charge Sweep (grouped) Without returning to zero, step the manual charge command through: -30 → -150 → -300 kW. | Charging is shared equally, SOC increases, charging stable with no protection trips: - -30 kW: -10 / -10 / -10 kW (charging begins) - -150 kW: -50 / -50 / -50 kW - -300 kW: -100 / -100 / -100 kW (full charge, stable). |  |  |
| 2.6 Maximum Charge Limit Set manual power = -400 kW. | PLC limits charge to -300 kW; no PCS exceeds rated power. |  |  |
| 2.7 One Unit Unavailable Disable BESS-3, command 150 kW discharge. | BESS-1 = 75 kW, BESS-2 = 75 kW, BESS-3 = 0 kW. |  |  |
| 2.8 Two Units Unavailable Disable BESS-2 and BESS-3, command 150 kW discharge. | BESS-1 = 100 kW (limited), BESS-2/3 = 0 kW. Remaining 50 kW supplied by grid or left unmet; available capacity updated. |  |  |
| 2.9 Ramp Rate Verification Increase power 0 → 300 kW using the configured ramp rate. | Output follows the configured ramp; no oscillation; no unit trips. |  |  |
| 2.10 Sudden Stop Command While discharging at 300 kW, command 0 kW. | Output decreases per ramp settings; stable transition to zero power; no alarms. |  |  |
| 2.11 Mode Change to Automatic (Peak Shaving) Operate at 150 kW Manual, then switch to Peak Shaving Mode. | Manual command released; automatic controller assumes control without interruption; no power spikes or trips. |  |  |

# Section 3 – Peak Shaving Mode Tests

Mode: Peak Shaving. The PLC monitors grid import/export via the grid meter. When the measured value exceeds the configured Peak Shaving limit it commands the units to charge/discharge to hold the grid at or below the limit, distributing power equally unless modified by SOC-balancing logic.

Note: all Peak Shaving limits are based on current; the kW values below are for understanding only. Default configuration for this section: Peak (Grid) Limit = 150 kW.

| Test Name | Expected Results | Approved (Pass/Fail) | Comments |
| --- | --- | --- | --- |
| 3.1 Incremental Load Sweep vs. Peak Limit (grouped) With Peak Shaving active and limit = 150 kW, step the site load through: 100 → 140 → 150 → 170 → 240 → 330 → 450 → 520 kW. | Grid import held at/below 150 kW while capacity allows; battery supplies the excess, shared equally, no unnecessary cycling: - 100 kW: grid 100, BESS 0 - 140 kW: grid 140, BESS 0 - 150 kW: grid 150, BESS 0 (no cycling) - 170 kW: grid 150, BESS 20 (≈6.7 each) - 240 kW: grid 150, BESS 90 (30 each) - 330 kW: grid 150, BESS 180 (60 each) - 450 kW: grid 150, BESS 300 (100 each, no overload) - 520 kW: BESS max 300, grid 220 (peak cannot be held), no PCS overload. |  |  |
| 3.2 Curtailment – Grid Limit 100 kW Load = 480 kW; enable Curtailment; Max Consumed = 100 kW; current limit from grid = 100 kW. | Battery = 300 kW (max); Grid import = 100 kW; Curtailment = 80 kW. Peak limit cannot be maintained; no PCS overload. |  |  |
| 3.3 Curtailment – Grid Limit 50 kW Load = 480 kW; enable Curtailment; Max Consumed = 100 kW; current limit from grid = 50 kW. | Battery = 300 kW (max); Grid import = 50 kW; Curtailment = 100 kW (max). Curtailment covers up to 100 kW; remaining 30 kW covered from grid (50 + 30 kW). Peak limit cannot be maintained; no PCS overload. |  |  |
| 3.4 Dynamic Load Response (grouped) Execute consecutively: (a) reduce load 450 → 300 kW; (b) rapid increase 120 → 400 kW; (c) rapid decrease 400 → 120 kW; (d) oscillating load 150/250/170/280/140 kW every 10 s. | (a) Battery output reduces smoothly, no oscillation/delay, grid ≈150 kW. (b) Battery responds within configured response time, grid overshoot resolved within 4 s, stable control. (c) Battery ramps down, no reverse power, no oscillation. (d) Battery follows demand, no hunting, stable control. |  |  |
| 3.5 Unit Redundancy (grouped) Execute consecutively with load 300 kW, Peak = 150 kW: (a) disable Unit 3; (b) also disable Unit 2 (load 250 kW); (c) reconnect Unit 3. | (a) Required battery 150 kW → Unit1 75, Unit2 75, Unit3 0. (b) Unit1 supplies max 100 kW, grid import 150 kW, no overload. (c) PLC automatically redistributes power on reconnection, no interruption. |  |  |
| 3.6 SOC-Based Behaviour (grouped) Verify: (a) SOC = 10%, load exceeds peak; (b) SOC = 100%, peak load; (c) SOC recovers above minimum; (d) unequal SOC 95/70/40%, 150 kW; (e) all SOC equal (80%). | (a) Discharge blocked, grid exceeds peak limit, Low SOC alarm. (b) Battery allowed to discharge, no charge command. (c) Battery automatically resumes discharge. (d) PLC allocates more discharge to higher-SOC units per balancing algorithm. (e) Equal power sharing. |  |  |
| 3.7 SOC Protection Limits (grouped) (a) Reduce all units below min SOC (≈10%), command 300 kW discharge; (b) raise all units to max SOC (≈100%), command 300 kW charge. | (a) Discharge blocked, Low SOC alarm active, no battery damage. (b) Charging blocked, High SOC alarm active. |  |  |
| 3.8 Grid Meter Failure & Recovery Disconnect the grid meter, then reconnect it. | On failure: PLC detects the meter fault, Peak Shaving disabled or enters configured fallback (fixed charge/discharge power), alarm generated. On recovery: automatic recovery, Peak Shaving resumes with the latest settings. |  |  |
| 3.9 PLC Restart During Peak Shaving Restart / disconnect the PLC while units are operating. | Controlled restart; no unsafe battery operation; Peak Shaving resumes after initialization. |  |  |
| 3.10 Unit Communication Loss Disconnect Unit 2 during Peak Shaving. | Unit removed from control; remaining units continue; alarm generated. |  |  |
| 3.11 PCS Fault During Peak Trip Unit 3 during Peak Shaving. | Remaining units continue; power redistributed automatically. |  |  |
| 3.12 Maximum Ramp Test Increase load 100 → 450 kW. | Battery reaches maximum output without oscillation. |  |  |
| 3.13 Peak Limit Change During Operation (grouped) (a) Lower limit 150 → 100 kW; (b) raise limit 100 → 200 kW. | (a) Battery increases discharge smoothly, no instability. (b) Battery reduces output accordingly. |  |  |
| 3.14 Disable Peak Shaving Disable Peak Shaving while operating. | Battery ramps to zero output; grid supplies the full site load; no alarms or abrupt power changes. |  |  |

# Section 4 – Idle Charging & SOC Target Control Tests

Mode: Idle Charging / SOC Recovery. When Peak Shaving is enabled, the PLC automatically maintains the battery at a configurable Target SOC using spare grid capacity, and immediately stops whenever Peak Shaving charge/discharge becomes necessary.

Assumptions (adjusted to available load/grid at Hall 6): Peak Limit = 150 kW; Idle Charge Enable = Yes; Target SOC = 80%; Minimum SOC = 20%; Maximum SOC = 100%; Maximum Charge Power = 300 kW; Idle power = 100 kW.

| Test Name | Expected Results | Approved (Pass/Fail) | Comments |
| --- | --- | --- | --- |
| 4.1 Enable Idle Charging & Charge to Target (grouped) Enable Peak Shaving and Idle Charging; Target SOC = 80%; all units SOC = 50%; load = 80 kW; Peak = 150 kW. Allow charging to 80%, then reduce SOC to 75%. | Idle Charging enabled; charging starts automatically; PLC calculates available charging power (150 − 80 = 70 kW); no alarms. At 80% target: charge command → 0 kW, SOC stable, BESS online and ready. At 75%: charging resumes automatically. |  |  |
| 4.2 Target SOC Changes (grouped) While charging: (a) raise Target 80 → 90%; (b) lower Target to 70%; (c) change Target 80 → 60 → 95% in operation. | (a) Charging continues until the new target is reached. (b) Charging stops immediately; if possible the system discharges to reach the target (requires grid limit ≠ 0). (c) PLC immediately applies each new Target SOC, starting/stopping charging as required without instability. |  |  |
| 4.3 Peak Interaction During Charging (grouped) (a) Charging at 120 kW, increase load 80 → 220 kW; (b) reduce load 220 → 80 kW with SOC still below target; (c) alternate load 80/220 kW every 15 s. | (a) Charging stops immediately, battery transitions to discharge, grid held at Peak Limit, no oscillation. (b) Battery automatically resumes charging. (c) PLC correctly alternates between charging and discharging, no instability. |  |  |
| 4.4 Charge Limited by Maximum Charge Power Available charging demand exceeds the configured maximum (300 kW). | Charging limited to 300 kW. |  |  |
| 4.5 Charging Redundancy (grouped) (a) Disable Unit 3; (b) also disable Unit 2; (c) reconnect Unit 3. | (a) Charging shared equally between Units 1 and 2 only. (b) Remaining battery charges within its limit. (c) Charging redistributed automatically on reconnection. |  |  |
| 4.6 SOC Balancing While Charging (grouped) (a) SOC 20/45/70%; (b) all SOC = 60%; (c) SOC 100/60/60%. | (a) PLC prioritizes charging the lower-SOC battery per balancing algorithm. (b) Equal charging current. (c) Full battery receives no charge; remaining units continue charging. |  |  |
| 4.7 Fault Handling While Charging (grouped) (a) Trip Unit 1; (b) disconnect grid meter; (c) restart PLC; (d) disconnect and reconnect one unit's communication. | (a) Remaining units continue charging. (b) Charging stops or enters fallback (power-meter fixed power), alarm generated. (c) System returns to Idle Charging after initialization. (d) Affected unit stops charging during comm loss and automatically rejoins the charging group after recovery. |  |  |
| 4.8 Charge Ramp Verification Command Idle Charging from 0 kW to configured maximum charge power. | Charge power follows the configured ramp rate with no overshoot or oscillation. |  |  |
| 4.9 Mode Transitions (grouped) (a) Disable Idle Charging while charging; (b) disable Peak Shaving while Idle Charging active; (c) power-cycle the PLC; (d) switch to Manual Mode (disable Peakshave first) and command discharge. | (a) Charging stops; Peak Shaving remains enabled. (b) System follows configured behaviour (charging stops or changes to Manual if selected). (c) System restores previous configuration; Idle Charging resumes if required. (d) Idle Charging cancelled, Manual Mode active, requested power achieved smoothly per configured ramp rate. |  |  |

# Test Sign-off

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Test Engineer |  |  |  |
| Witness / Client |  |  |  |
| Approved by |  |  |  |