# SOFTWARE DESIGN DOCUMENT (SDD)

Product: E-PU10 V2 Battery Energy Storage System (BESS)
Platform: Beckhoff TwinCAT 3 PLC
Software Version: __________
Document Number: __________
Revision: __________
Date: __________

# 1. Purpose and Scope

This document describes the software architecture, design, communication interfaces, control philosophy, safety functions, and verification approach of the E‑PU10 V2 controller.

# 2. PLC Software Architecture

Project Structure

- PLC Project

  - GVLs

    - GVL

    - Settings

  - Datalogger

  - ErrorHandling

  - EventLogger

  - Functions-FBs-Programs

  - MonitoringControl

    - Enums

    - Structs

    - HMI

    - IoT

    - ProfinetController

    - ControlManager (PRG)

  - Objects

    - 4Grouter

    - ACDCCharger

    - ACSwitchgear (clientbox)

    - BMS

    - CoolingSystem

    - DCSwitchgear

    - Enclosure

    - GenComm
HartingIO

    - InterMachineCom

    - InternalPowerSupply

    - NeutralTransformer

    - PeakshaveBox

    - PLCStatus

    - PowerQualityMonitor

    - PowerStack

    - ProtectionSystems

    - WearLogging

  - Safety

  - System

    - GenGridControl

    - PowerControl

  - MAIN_Fast (2 ms) (PRG)

  - MAIN_Slow (10ms) (PRG)

# 3. Software Modules

• ControlManager: Top-level supervisory program coordinating monitoring, external interfaces and persistent settings.

- Calls the HMI, ProfinetController, IoT and TestScripts sub-modules each slow cycle.

- Selects the active control source (HMI, PROFINET or IoT) and forwards the corresponding setpoints to the system.

- Manages write-back of persistent settings (hard/soft) via the TwinCAT persistent-data service.

• MonitoringControl: Container for the supervisory sub-modules used by the slow task.

- Aggregates the HMI, IoT and ProfinetController function blocks.

- Provides the common monitoring/control structures (ST_System_Monitor / ST_System_Control) exchanged with the fast task.

• ErrorHandling: Centralized fault detection, classification and acknowledgement.

- Collects errors raised by every object FB through a common FB_AddErrorST interface.

- Classifies events as Warning, Error or Fault and drives the corresponding global shutdown flags.

- Supports user acknowledgement and history clearing from HMI and remote interfaces.

• EventLogger: Records events, state changes and user actions for later analysis.

- Provides the WriteLogItem function used by all modules to push entries with source, severity and text.

- Persists log items to file storage using TwinCAT file I/O function blocks.

• Datalogger: Periodic acquisition and historisation of monitoring data.

- Samples the ST_System_Monitor structure at a configurable rate.

- Provides array-based buffers used by the HMI trend screens and exported historic files.

• WearLogging: Persistent tracking of wear-related variables across power cycles.

- Generic FB_VarLogger supports on-time tracking, edge counting and min/max recording per item.

- Used by Safety, Power Stack, BMS and other modules to expose lifetime counters and statistics.

• HMI: TwinCAT 3 HMI server interface for the local touch panel.

- Exposes monitoring data and operator commands through the ST_HMI_monitor and ST_HMI_control structures.

- Implements the screen navigation logic (Overview, Operation Controls, Machine Status, Settings, Diagnostics, Historics).

- Provides user-level access management and forwards parameter changes to the persistent settings store.

• IoT: Remote telemetry and command interface based on MQTT.

- Connects to the OpenRemote broker using the TwinCAT FB_IotMqttClient (secured connection).

- Publishes system status, active events and KPIs; subscribes to remote commands such as shutdown requests.

- Connection state and last-error information are surfaced through ST_ExtController_get.

• ProfinetController: External controller interface over PROFINET.

- Exchanges setpoints and feedback with an upstream EMS/SCADA PLC when an EL669x PROFINET coupler is fitted.

- Coupler type and availability are taken from the Configuration settings.

- Activates only when the operator selects PROFINET as the control source in ControlManager.

• InterMachineCom: MQTT-based communication between parallel-operating units.

- Implements master/slave roles via FB_ConnectMqttBroker and ST_InterMachineCom_Master / Slave structures.

- Used when several E-PU10 units are coupled for output parallel operation.

• PowerControl: Real-time charge/discharge power control algorithms.

- Computes active and reactive power requests for the inverter from the active operating mode (P/Q, PF, droop, isochronous).

- Applies SOC-based limits, voltage/frequency droop and Power-Stack feedback to keep the operating point within safe margins.

- Provides separate inverter and generator power requests to support hybrid (battery + genset) operation.

• GenGridControl: Supervisory grid- and genset-interaction logic.

- Drives input and external contactors via FB_ContactorControl, including synchronisation through a PID-based voltage trim.

- Decides between grid-following and grid-forming behaviour based on bus presence and operator selection.

- Implements automatic start/stop on SOC, load, charge-load and full-battery criteria.

- Provides the target structure consumed by PowerControl.

• Safety: TwinSAFE supervisory program and EDM signal handling.

- Runs under a dedicated safety task and interfaces with the TwinSAFE I/O via ST_Safety_ToSafetyPrg / ST_Safety_get.

- Monitors the external emergency-stop input, manual reset, and contactor EDM feedbacks of the net contactor and master/slave MCCBs.

- Records E-Stop activations and power-module door openings through FB_VarLogger for lifetime statistics.

- Drives the global emergency-shutdown flag used by the rest of the application.

• BMS: Battery Management System communication and supervision.

- Wraps the MBMU/SBMU data exchange and exposes a consolidated battery summary (voltage, current, SOC, SOH, temperatures).

- Translates BMS status words into harmonised warnings and faults (communication loss, configuration warning, HV interlock, …).

- Maintains persistent battery statistics: cycle count, cumulative charge/discharge energy, lifetime min/max voltages and currents, calibration date.

- Exposes a HV-DC power status used by Power Stack to gate DC-link enable.

• PowerStack: Interface to the Power Conversion System (inverter and modules).

- Coordinates the power modules, net contactor, master/slave MCCBs and rotation switch.

- Forwards active/reactive power requests from PowerControl and exposes the inverter operating state (AFE, Island, Microgrid; Droop, Isochronous).

- Manages cooling requests, transport mode, double-power-module configuration and AC-rotation detection.

- Provides EDM feedbacks for the Safety program and grid-code trip information.

• CoolingSystem: Thermal management of the cabinet and the power electronics.

- Controls fans and the optional heat-pump (Trane or LG variants) based on internal temperatures and Power Stack requests.

- Switches between off, low-power (internal 400 V AC supply only) and full-power modes depending on cooling demand.

• Enclosure: Cabinet auxiliaries (climate, doors, LED indicator).

- Aggregates climate, door-switch and LED-indication sub-FBs.

- Provides the LED status indication via the Arduino-based LED controller and surfaces door interlock feedbacks.

• ACSwitchgear (Clientbox): Control and monitoring of the AC switchgear cabinet.

- Reads breaker positions, alarms and the customer-side I/O.

- Exposes setpoints, parameters and events through the standard get/set/params/events structures.

• DCSwitchgear: Control and monitoring of the DC switchgear.

- Provides feedbacks on DC isolators and contactors used in the battery DC link.

• NeutralTransformer: Monitoring and control of the neutral-earthing transformer.

- Reports operating status to the System Monitor.

- Used by the grid-forming logic to keep neutral-point bonding consistent with the active operating mode.

• InternalPowerSupply: Internal 24 V / auxiliary supply and UPS supervision.

- Manages the CEE auxiliary input, internal power demand and UPS charge mode.

- Implements an orderly low-battery shutdown timer when running on the UPS.

• ProtectionSystems: Electrical and physical protection devices.

- Aggregates insulation monitoring, residual-current monitoring, overcurrent protection, surge protection and fire detection.

- Surfaces trip and warning signals to ErrorHandling so they participate in the system shutdown decision.

• PowerQualityMonitor: Power-quality and energy measurement (Janitza UMG 801).

- Reads voltages, currents, power, energy and unbalance values from the meter.

- Detects grid-code violations such as current unbalance limits and feeds them into the Power Stack trip logic.

- Maintains persistent counters for energy supplied to and consumed from the BESS.

• PeakshaveBox: Optional external peak-shaving and energy-management box.

- Reads metering data from the customer load measurement.

- Provides setpoints that bias the PowerControl targets to limit grid import/export.

• HartingIO: Customer Harting connector I/O for digital signals.

- Maps the customer-accessible digital inputs and outputs (start/stop, status, alarms).

- Used as one of the possible control sources when remote interfaces are not active.

• ACDCCharger: AC/DC battery charger interface.

- Drives the Phoenix Contact / Winline UXR100040G chargers used for auxiliary battery charging.

- Enforces charging limits based on BMS state-of-charge, system voltage, current and maximum-charge-current feedback.

• PLCStatus: PLC self-diagnostics and runtime health.

- Reads the EL9410 power-supply status terminal.

- Provides PLC state information (cycle status, persistent data, restart events) to the rest of the application.

- Supports the controlled PLC update workflow through FB_PLCUpdate.

• GenComm: Genset interface and Geneset controller communication.

- Wraps the DEIF AGC-150 controller interface for generator monitoring and control.

- Exchanges generator status, load-share and start/stop commands used by GenGridControl in hybrid operation.

• 4Grouter (Teltonika): Cellular router supervision.

- Monitors the Teltonika 4G router availability and signal quality.

- Provides the remote-access transport layer used by the IoT module.

# 4. Task Architecture

Fast Task (PlcTask) – 2 ms cycle, priority 4. Executes MAIN_Fast.
- Real-time device control (Power Stack, BMS, switchgear, cooling, protections, internal supply)
- Closed-loop power and grid/genset control (PowerControl, GenGridControl)
- Safety-relevant signal handling and EDM feedbacks
- Update of the shared ST_System_Monitor structure exchanged with the slow task

Slow Task (MonitorControlTask) – 10 ms cycle, priority 8. Executes MAIN_Slow.
- ControlManager (HMI, IoT, PROFINET, test scripts, persistent settings)
- ErrorHandling, EventLogger and Datalogger
- Long-running communications and diagnostics

Safety Task – runs the TwinSAFE Safety program on a dedicated safety runtime, independently of the standard PLC tasks.

# 5. Operational States

The system state is represented by the eSystemState enumeration with the following values: Off, Shutdown, StandBy, Conditioning, Starting, Running, Charging_Only, Discharging_Only, Stopped, EMstop, Reset, Init, Transport and Dehumidifying.

Operation mode is selected via the eOperationMode enumeration (Auto, Gridfollowing, GridForming). The active Power-Stack modes are described by ePowerModes (DroopZeroStart, Droop, Isochronous) and eInverterModes (AFE, Island, Microgrid).

State transitions are driven by ControlManager (operator and remote commands), GenGridControl (automatic start/stop on SOC, load and bus availability) and the Safety program (emergency-stop and critical-fault paths).

Add state-transition diagram in Appendix B.

# 6. Object-Level Design

BMS:
- SOC, SOH, system voltage, current and temperature monitoring
- Battery warnings and faults derived from MBMU / SBMU status words
- Persistent cycle counter and lifetime energy / min-max statistics

PowerStack:
- Active and reactive power requests forwarded to the inverter
- Net contactor, master / slave MCCB and AC-rotation switch control with EDM feedbacks
- Inverter and power-mode state machines (AFE / Island / Microgrid; Droop / Isochronous)

CoolingSystem:
- Cabinet and power-electronics thermal management
- Fan and heat-pump (Trane / LG) control with multi-level power requests

ProtectionSystems:
- Insulation monitoring, residual-current monitoring, overcurrent and surge protection, fire detection
- Trip aggregation into the global shutdown logic

PowerQualityMonitor:
- Janitza UMG 801 measurements and energy counters
- Current-unbalance and grid-code violation detection

Safety:
- TwinSAFE program with E-Stop, EDM monitoring and safe-state transition
- Interface structures ST_Safety_ContactorEDM, ST_Safety_ToSafetyPrg, ST_Safety_get

# 7. Safety Design

Safety Program (TwinSAFE):
- External and panel emergency-stop handling
- Contactor EDM monitoring for the net contactor and master / slave MCCBs
- Manual reset with debounced reset timer
- Drives the global emergency-shutdown flag and the safe-state transition of the application

Interface structures:
- ST_Safety_ContactorEDM
- ST_Safety_ToSafetyPrg (outputs to the safety runtime)
- ST_Safety_get (feedbacks from the safety runtime)

Lifetime statistics (E-Stop activations, power-module door openings, safety-stop count) are tracked through FB_VarLogger and persisted by the WearLogging module.

# 8. Communication Interfaces

Field bus and I/O backbone:
- EtherCAT for all on-board I/O terminals (EL / KL series), the TwinSAFE coupler and the Janitza UMG 801 power-quality meter.

Battery Management System (BMS):
- MBMU / SBMU status data exchange; CAN-bus communication faults between MBMU and SBMUs are surfaced as warnings/faults inside FB_BMS_IO.

Power Stack / Power Modules:
- Modbus RTU master via the KL6x22B serial terminal (ModbusRtuMasterV2_KL6x22B).

Cooling system (heat pump):
- Modbus interface to the selected heat-pump variant (Trane / LG).

External / SCADA controller:
- PROFINET coupler (Beckhoff EL669x) handled by FB_ExternalController; active only when configured.

Remote telemetry and control:
- MQTT over TLS to the OpenRemote broker (FB_IotMqttClient).
- Inter-machine communication between parallel units also uses MQTT.

Genset:
- DEIF AGC-150 controller interface (FB_AGC150) for monitoring and load-share.

Connectivity:
- Teltonika 4G router (FB_Teltonika) provides the wide-area transport for the IoT module.

Customer I/O:
- Harting connector digital I/O (FB_HartingIO) for hard-wired start/stop, status and alarm exchange.

Detailed register maps and message catalogues are listed in Appendices D and E.

# 9. HMI Design

The HMI is implemented with TwinCAT 3 HMI and organised in the following screen groups, matching the content files of the TcHmi_ePU10 project:

1. Overview – system overview and live monitoring plots
2. Operation Controls – grid input, genset input, output parallel operation, DC-bus extension and DC charger, peak-shave box, system and earthing-system settings
3. Diagnostics
4. Machine Status – Power Stack (single / double inverter, raw data), Battery, Auxiliaries, Monitoring, Cooling System, External Controller, IoT Controller, PROFINET Controller, Peak-Shave Box, PLC and DC Bus
5. Settings – Configuration, Power Stack, Cooling System, Enclosure, ZPT, Internal PSU, Battery, Protections, System, HMI, External Control
6. Historics and additional screens (Scheduler, Login, Shutdown / Stop warnings, Waiting screen, IoT data-sharing settings)

(Add screenshots in Appendix F.)

# 10. Verification & Validation

- Unit Testing – isolated test scripts driven by FB_TestScripts and inspectable from the HMI.
- Integration Testing – combined exercise of MAIN_Fast and MAIN_Slow against simulated I/O.
- Factory Acceptance Testing (FAT) – functional verification on the assembled unit.
- Site Acceptance Testing (SAT) – verification on site against the customer specification.
- Communication Testing – BMS, Power Stack Modbus, PROFINET coupler, MQTT (IoT and inter-machine), Genset and 4G router.
- Safety Verification – TwinSAFE program validation, EDM monitoring, emergency-stop and safe-state transition.
- Cybersecurity Verification – TLS configuration of the MQTT link and user-access checks on the HMI.

# 11. Appendices (To Be Completed)

Appendix A – System Architecture Diagram
Appendix B – State Machine Diagram
Appendix C – Alarm Matrix
Appendix D – Modbus Register Maps
Appendix E – CAN Message Definitions
Appendix F – HMI Screenshots
Appendix G – PLC Task Timing and CPU Load