## 1. Executive Summary
e-PU10 400A AC/DC Charger - TRL2 Market Study
Executive Summary - ranked shortlist of commercial AC/DC charging solutions. Prepared for the TRL2 market research review. Unverified data marked 'Unknown'.
Objective: identify and evaluate commercial AC/DC charger solutions for a galvanically isolated, liquid-cooled, unidirectional 600-800 VDC charger (400 A AC Powerlock input, modular >=55 kW) embeddable in the e-PU10 BESS. 12 products were assessed across 3 architectures: (a) liquid-cooled EV power modules built N-up into a charger, (b) programmable DC power supplies, and (c) turnkey industrial chargers. Key finding: the >97.5% full-load efficiency / <7 kW heat target is the hardest requirement - no surveyed product clearly guarantees it at full load, so it is a primary design risk. The liquid-cooled power-module architecture offers the best overall fit (isolation, liquid cooling, modular power steps, cost) and is recommended as the basis of the e-PU10 charger.
Rank | Product | Category | Overall score (0-100) | Recommendation | Key finding
1 | Infypower LCG1K0135G | Liquid-cooled power module (build N-up charger) | 88.2 | Strongly recommended | Excellent - module architecture lets VDL build an isolated, liquid-cooled 400A-class charger with modular 40 kW steps
2 | UUGreenPower UR100040-LQ-DD | Liquid-cooled power module (build N-up charger) | 87.9 | Strongly recommended | Excellent - same modular architecture; strong full-load efficiency near the 97.5% target
3 | MIDA EV Power U3T-A040B-S | Liquid-cooled power module (build N-up charger) | 84.9 | Strongly recommended | Good module alternative with native AC/DC front-end
4 | Winline LCR100040A | Liquid-cooled charging module (build N-up charger) | 83.9 | Strongly recommended | Good module alternative; efficiency further from 97.5% target
5 | Huawei HiCharger 40kW LC module | Liquid-cooled power module (build N-up charger) | 82 | Strongly recommended | Good module option; documentation access weaker than Infypower/UU
6 | Friem HPB High Power Battery Charger | Industrial rectifier / turnkey charger system | 73.2 | Recommended | Good as a turnkey reference / fallback, but envelope, weight and cost are integration risks
7 | Heinzinger ERS | High-power DC source (water-cooled) | 66.3 | Consider / conditional | Moderate - meets power/voltage/cooling but envelope, weight and cost are major risks
8 | EA Elektro-Automatik PSI 10000 | Programmable DC power supply (lab/industrial) | 61.5 | Consider / conditional | Limited - air cooled and costly; better as a bench/validation reference than series charger
9 | Regatron TopCon TC.P | Programmable DC power supply (modular) | 60.6 | Consider / conditional | Moderate - 800 V match and liquid option, but efficiency and cost work against series use
10 | Delta Elektronika SM15K | Programmable DC power supply (industrial) | 59.5 | Consider / conditional | Limited for series charger (air, cost) but a strong, well-documented EU bench/validation reference
11 | Magna-Power MS/MT series | Programmable DC power supply (industrial) | 56.2 | Consider / conditional | Limited - air cooled and modest efficiency; good comms but poor thermal/cost fit
12 | Kempower Power Unit + LC Satellite | Complete EV DC fast charger (turnkey) | 55.7 | Consider / conditional | Poor as embedded option - it is a standalone EV charger, not an embeddable BESS charger module
TOP 3 RECOMMENDATIONS
Infypower LCG1K0135G | Best overall fit: isolated, liquid-cooled, 150-1000 V module with the highest peak efficiency (97.5%), hot-plug, MPPT and TUV/CE certification. Built N-up it yields a 400A-class charger with modular 40 kW steps (matches e-PU10 nice-to-have) at lowest cost. Main work: VDL AC front-end, enclosure and a CAN->Modbus-TCP gateway.
UUGreenPower UR100040-LQ-DD | Strong full-load efficiency (>=97%, closest to the 97.5% target), isolated, 200-1000 V, zero-standby, low cost. Same modular architecture and integration effort as the leader; an excellent primary or second-source module.
MIDA EV Power U3T-A040B-S | Native AC/DC 40 kW liquid-cooled module, isolated, 150-1000 V, low noise and low cost. Same modular build-up approach; a solid second-source to the leaders, with a smaller supplier as the main caveat.
Alternative (turnkey) | Friem HPB - best turnkey / industrial-rectifier reference: native Modbus TCP, IEC 61439 and liquid cooling from a reputable EU manufacturer. Use as a benchmark / fallback to the module architecture; cabinet envelope, weight (likely >500 kg) and cost are the integration risks to verify by quotation.

## 2. Detailed Research
Detailed Market Research
Full technical specifications per product. 'Unknown' = not verified from public sources at time of study.
Parameter | Infypower LCG1K0135G | UUGreenPower UR100040-LQ-DD | Friem HPB High Power Battery Charger | Huawei HiCharger 40kW LC module | Winline LCR100040A | MIDA EV Power U3T-A040B-S | EA Elektro-Automatik PSI 10000 | Regatron TopCon TC.P | Heinzinger ERS | Magna-Power MS/MT series | Delta Elektronika SM15K | Kempower Power Unit + LC Satellite
Manufacturer | Infypower (Shenzhen INFY Power) | UUGreenPower | FRIEM S.p.A. | Huawei Digital Power | Shenzhen Winline Technology | MIDA EV Power | EA Elektro-Automatik | Regatron AG | Heinzinger electronic GmbH | Magna-Power Electronics | Delta Elektronika B.V. | Kempower Oyj
Model | LCG1K0135G | UR100040-LQ-DD | HPB (High Power Battery charger) | HiCharger 40 kW Liquid-Cooled Module | LCR100040A | U3T-A040B-S | PSI 10000 series (e.g. 920 V, 30 kW/chassis) | TC.P series (e.g. TC.P.32.800.400.S) | ERS series (e.g. ERS 1000-x) | MS/MT series (e.g. 800 V models) | SM15K series (0-800 V) | Power Unit 600 kW + Liquid-Cooled Satellite
Category | Liquid-cooled power module (build N-up charger) | Liquid-cooled power module (build N-up charger) | Industrial rectifier / turnkey charger system | Liquid-cooled power module (build N-up charger) | Liquid-cooled charging module (build N-up charger) | Liquid-cooled power module (build N-up charger) | Programmable DC power supply (lab/industrial) | Programmable DC power supply (modular) | High-power DC source (water-cooled) | Programmable DC power supply (industrial) | Programmable DC power supply (industrial) | Complete EV DC fast charger (turnkey)
Product page | https://www.infypower.com/products/power-module-solution-liquid-cooled-power-module-dcdc-module-40kw/156 | https://www.uugreenpower.com/40kW-Liquid-Cooling-DC-Charging-Module-2 | https://friem.com/products/energy-storage-systems/hpb-high-power-battery-charger/ | https://digitalpower.huawei.com/en/ | https://en.szwinline.com/product/lcr100040a-40kw1000v-liquid-cooling-charging-module/ | https://www.midaevpower.com/u3t-a040b-s-40kw-ac-dc-liquid-cooling-charging-module-fast-ev-charger-power-module/ | https://elektroautomatik.com/en/products/dc-power-supplies/ | https://www.regatron.com/programmable-dc-power/tc-p/ | https://www.heinzinger.com | https://magna-power.com/products/programmable-dc-power-supplies | https://www.delta-elektronika.nl/en/products/dc-power-supplies-15kw-sm15k-series.html | https://kempower.com/charging-solutions/
Datasheet | Request via product page (TUV/CE certified) | Request via product page | Project-specific (request from FRIEM) | Restricted / via Huawei sales | Via product page | Via product page | https://docs.rs-online.com/dbf9/A700000010137212.pdf | https://www.regatron.ch/download-public/datasheets/DS_TCP_20_800_400_S_E_05.pdf | https://ppmpower.co.uk/wp-content/uploads/Heinzinger_ERS.pdf | https://magna-power.com/assets/docs/ms_series.pdf | https://www.delta-elektronika.nl/en/products/dc-power-supplies-15kw-sm15k-series.html | https://www.chargehub.solutions/_files/ugd/701e4c_b237aa4abd804bf4ad52ddb494767a91.pdf
Max AC input current | ~58 A/module @400VAC (system: parallel up to 48 modules) | ~58 A/module @400VAC (system: multi-module) | Configurable (designed for 400A-class AC input) | ~58 A/module @400VAC (system: multi-module) | ~58 A/module @400VAC (system: multi-module) | ~58 A/module @400VAC (system: multi-module) | Per chassis; parallel up to 64 units | Per unit; matrix/parallel scaling | 3 x 380-480 VAC; high-current input | Per unit; parallel scaling | Per unit; parallel up to ~30 units | High (cabinet AC input)
AC input voltage | Module DC-link / AC front-end 3P 400 VAC class | 260 - 530 VAC, 3P + PE (module class) | 3P 400 VAC class (project configured) | 3P 400 VAC class (module) | 260 - 530 VAC, 3P (module class) | 260 - 530 VAC, 3P + PE | Wide AC, 3-phase | 3-phase | 3 x 380 - 480 VAC, 3P/N/PE | 3-phase | 3-phase | 3-phase grid
DC output voltage range | 150 - 1000 VDC | 200 - 1000 VDC | Configurable up to ~800 VDC | 150 - 1000 VDC (typical) | 300 - 1000 VDC | 150 - 1000 VDC | Up to 920 VDC (model-dependent) | 0 - 800 VDC | 20 - 1000 VDC | Up to 800 VDC (model-dependent) | 0 - 800 VDC | Up to 1000 VDC
Max DC output current | Up to 133 A/module | 0.5 - 80 A/module | Configurable (modular 50-500 kW) | Up to ~100 A/module | Up to 133 A/module | Up to 133 A/module | Model-dependent (autoranging) | Up to ~32-40 A/unit | Up to ~1200 A | Model-dependent | Model-dependent | Up to 500 A (per satellite)
Max power (kW) | 40 kW/module (multi-module to >250 kW) | 40 kW/module (multi-module to >250 kW) | 50 - 500 kW (modular) | 40 kW/module | 40 kW/module | 40 kW/module | Up to 30 kW/chassis, parallel to MW | 10-32 kW/unit (parallel/matrix to MW) | 50 - 250 kW/channel | Up to ~100s kW (parallel) | 15 kW/unit (parallel to ~1 MW) | Up to 600 kW (cabinet), 400 kW/output
Galvanic isolation | Yes (HF transformer) | Yes (HF transformer) | Yes (typical for industrial chargers) | Yes | Yes (water-electricity separation) | Yes | Yes (<3.5 mA leakage) | Yes (HF transformer) | Yes | Yes | Yes (>=3750 Vrms, isolated interfaces) | Yes
Cooling | Liquid | Liquid | Liquid (high-power versions) | Liquid | Liquid | Liquid | Air (forced) | Air or liquid (config-dependent) | Liquid (water) | Air | Air | Liquid (Glysofor N)
Efficiency | 96.5% full load, 97.5% peak | >=97% full load | Unknown (industrial high-eff., verify) | ~96% | >=95.5% full load | ~95.5-96.8% | >96% | >=93% | High (>=0.98 PF); exact % Unknown | >90% | ~92-93% | ~95-96%
Communication | CAN (up to 48 parallel) | CAN | Modbus TCP / CAN | CAN | Dual-DSP digital control (CAN typical) | CAN | Modbus TCP, Profinet, EtherCAT, CANopen, USB, Ethernet | CAN, CANopen, EtherCAT (opt), Ethernet, USB | CAN, EtherCAT; Modbus/Profibus optional | Modbus TCP, LXI/Ethernet, USB | Modbus TCP, Ethernet, CAN, Profibus, SCPI | CAN, Ethernet, OCPP, WiFi, cellular
EMC compliance | EMC/EMI Class B | Industrial (module-level) | Industrial EMC (verify per project) | Industrial | Industrial | Industrial | Industrial (CE/EMC) | EN 61000, EN 50178, CE | EN 61000-6-2/-4 | CE/EMC | CE/EMC | CE/EMC
CE compliance | Yes (CE, TUV, cTUVus) | Yes (CE) | Yes | Yes | Yes (CE) | Yes | Yes | Yes | Yes (EN 61010) | Yes | Yes | Yes
IEC standards | IEC 61000 (EMC); assembly to IEC 61439 at system level | IEC 61000 (EMC); assembly to IEC 61439 at system level | IEC 61439 compliant | IEC 61000 (EMC) | IEC 61000 (EMC) | IEC 61000 (EMC) | IEC 61000; lab-grade | IEC 61000 | IEC 61000; IP54 | IEC 61000 | IEC 61000 | IEC 61851/61000; IP54, IK10
Weight | ~28 kg/module | ~28 kg/module | Unknown (cabinet-class, likely >500 kg) | ~30 kg/module | ~28 kg/module | <=28 kg/module | Per chassis; multiple needed | ~64 kg/20 kW unit | Cabinet-class (heavy) | Per unit | Per 15 kW unit | Cabinet-class (heavy)
Dimensions | ~100 x 340 x 470 mm (module) | ~module form-factor (rack mount) | Cabinet (project configured) | Module form-factor | Module form-factor | ~100 x 340 x 470 mm | 19" rack 2U-4U/chassis | 19" rack, 399 mm H | Cabinet | Rack/cabinet | 19" rack 3U | Floor cabinet + satellites
Estimated price | ~EUR 1,800-3,000/module; ~EUR 11k-16k for 200 kW set | ~EUR 1,800-3,000/module; ~EUR 11k-16k for 200 kW set | Project-priced; likely > EUR 20k for full system | Unknown (volume-dependent) | ~EUR 1,800-3,000/module | ~EUR 1,800-3,000/module | High (~EUR 18k-25k/30 kW chassis) | High (lab-grade) | Very high (lab/industrial) | High | High (~EUR 15k-20k/15 kW) | Very high (>EUR 30k complete)
Availability / lead time | Stock/short (volume EV market) | Stock/short | Engineered-to-order (longer) | Volume-dependent | Stock/short | Stock/short | Catalogue (weeks) | Catalogue (weeks) | Engineered (longer) | Catalogue | Catalogue | Catalogue (weeks-months)
Key advantages | High peak efficiency, hot-plug, MPPT, wide range, low cost, modular power steps match e-PU10 nice-to-have | High full-load efficiency, isolated, wide range, zero-standby, low cost, modular | Turnkey industrial charger, IEC 61439 + Modbus TCP, liquid cooled, reputable EU manufacturer | Reputable manufacturer, high reliability, liquid cooled, isolated | Established module supplier, isolated, wide range, low cost | AC/DC module, low noise, isolated, low cost, modular | Best-in-class comms (Modbus TCP/Profinet/EtherCAT), isolated, autoranging, high efficiency, excellent documentation | 0-800 V exact match, isolated, liquid option, EtherCAT/CAN, scalable matrix | Single-unit 250 kW, 1000 V, liquid cooled, isolated, robust | Modbus TCP/LXI, isolated, 800 V available, scalable | 0-800 V exact match, Modbus TCP/CAN/Profibus, isolated, EU manufacturer, excellent quality | Turnkey, liquid cooled, 1000 V/500 A, isolated, dynamic power sharing, proven EU product
Key disadvantages | CAN only (no Modbus TCP/Profinet/EtherCAT); needs VDL system enclosure & controls; >97.5% only at peak not full load | CAN only; AC front-end / enclosure & controls to be built by VDL | Cabinet size/weight likely exceed e-PU10 module envelope & 500 kg; cost & efficiency unverified; longer lead time | CAN only; limited public datasheet; procurement/geopolitical considerations | Lower efficiency than peers; comms protocol to confirm (CAN); AC front-end/controls by VDL | CAN only; smaller supplier; AC front-end/controls by VDL | Air cooled; expensive; lab/test oriented not mobile/vibration-rated; many chassis to reach 250 kW | Lower efficiency (~93%); expensive; heavy per kW; test-oriented | Very expensive; cabinet weight likely >500 kg; efficiency % unverified; lab/test heritage | Air cooled; efficiency just >90%; test-oriented; cost | Air cooled; ~92% efficiency; many units for 250 kW; high cost/kW | EV-charger architecture (CCS/OCPP), cabinet size/weight far exceed e-PU10 envelope; expensive; unidirectional but EV-output oriented
Suitability for e-PU10 | Excellent - module architecture lets VDL build an isolated, liquid-cooled 400A-class charger with modular 40 kW steps | Excellent - same modular architecture; strong full-load efficiency near the 97.5% target | Good as a turnkey reference / fallback, but envelope, weight and cost are integration risks | Good module option; documentation access weaker than Infypower/UU | Good module alternative; efficiency further from 97.5% target | Good module alternative with native AC/DC front-end | Limited - air cooled and costly; better as a bench/validation reference than series charger | Moderate - 800 V match and liquid option, but efficiency and cost work against series use | Moderate - meets power/voltage/cooling but envelope, weight and cost are major risks | Limited - air cooled and modest efficiency; good comms but poor thermal/cost fit | Limited for series charger (air, cost) but a strong, well-documented EU bench/validation reference | Poor as embedded option - it is a standalone EV charger, not an embeddable BESS charger module

## 3. Compliance Matrix
Requirement Compliance Matrix
Pass / Fail / Unknown against mandatory & recommended criteria. Module products assessed at buildable-system level. Comms protocols shown individually (any one satisfies the mandatory comms requirement).
Requirement | Infypower LCG1K0135G | UUGreenPower UR100040-LQ-DD | Friem HPB High Power Battery Charger | Huawei HiCharger 40kW LC module | Winline LCR100040A | MIDA EV Power U3T-A040B-S | EA Elektro-Automatik PSI 10000 | Regatron TopCon TC.P | Heinzinger ERS | Magna-Power MS/MT series | Delta Elektronika SM15K | Kempower Power Unit + LC Satellite
Galvanically isolated | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass
Unidirectional AC->DC | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass
Liquid cooled | Pass | Pass | Pass | Pass | Pass | Pass | Fail | Unknown | Pass | Fail | Fail | Pass
600-800 VDC output range | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass
>=400 A AC-input capability | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass
Efficiency >97.5% | Unknown | Unknown | Unknown | Unknown | Fail | Unknown | Unknown | Fail | Unknown | Fail | Fail | Fail
Heat dissipation <7 kW | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Fail | Fail | Unknown | Fail | Fail | Unknown
Modbus TCP support | Fail | Fail | Pass | Fail | Unknown | Fail | Pass | Unknown | Unknown | Pass | Pass | Fail
CAN support | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Unknown | Pass | Pass
Profinet support | Fail | Fail | Unknown | Fail | Fail | Fail | Pass | Fail | Unknown | Fail | Pass | Fail
EtherCAT support | Fail | Fail | Unknown | Fail | Fail | Fail | Pass | Pass | Pass | Fail | Fail | Fail
CE compliant | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass
IEC 61439 compatible | Unknown | Unknown | Pass | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown
Industrial EMC (IEC 61000) | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass
Mobile / vibration resistant | Pass | Pass | Unknown | Pass | Pass | Pass | Fail | Fail | Fail | Fail | Fail | Unknown
Min. settable power <=55 kW | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass
Weight <500 kg | Pass | Pass | Fail | Pass | Pass | Pass | Unknown | Unknown | Fail | Unknown | Unknown | Fail
Suitable for BESS integration | Pass | Pass | Pass | Pass | Pass | Pass | Unknown | Unknown | Pass | Unknown | Unknown | Fail
Est. system cost <EUR 20,000 | Pass | Pass | Fail | Unknown | Pass | Pass | Fail | Fail | Fail | Fail | Fail | Fail
Overall fit for e-PU10 | Pass | Pass | Unknown | Pass | Pass | Pass | Unknown | Unknown | Unknown | Fail | Unknown | Fail
Mandatory compliance score (%) | 90.6 | 90.6 | 78.1 | 87.5 | 87.5 | 90.6 | 62.5 | 62.5 | 71.9 | 59.4 | 59.4 | 65.6
Legend: | Pass | Fail | Unknown

## 4. Cost & Risk
Cost & Risk Analysis
Estimated cost, lead time, supplier and technical-integration risks. Costs are indicative order-of-magnitude estimates pending quotation.
Product | Est. cost (system) | Lead time | Supplier risk | Technical integration risk | Cost fit <EUR 20k
Infypower LCG1K0135G | ~EUR 11k-16k (200 kW, modules only) | Stock/short | Low-Med (large EV supplier, TUV/CE; non-EU) | Med - build AC front-end, enclosure, CAN->Modbus gateway, thermal loop | Pass
UUGreenPower UR100040-LQ-DD | ~EUR 11k-16k (200 kW, modules only) | Stock/short | Low-Med (established module maker; non-EU) | Med - same system-build effort | Pass
MIDA EV Power U3T-A040B-S | ~EUR 11k-16k (200 kW, modules only) | Stock/short | Med (smaller supplier) | Med - system build | Pass
Winline LCR100040A | ~EUR 11k-16k (200 kW, modules only) | Stock/short | Low-Med (established; non-EU) | Med - system build; confirm comms | Pass
Huawei HiCharger 40kW LC module | Unknown (volume) | Volume-dependent | Med (geopolitical/procurement, limited datasheet) | Med - system build; documentation access | Unknown
Friem HPB High Power Battery Charger | Project-priced, likely >EUR 20k | Engineered-to-order | Low (reputable EU maker) | Med-High - envelope/weight vs e-PU10; verify efficiency | Fail (likely)
Heinzinger ERS | Very high (lab/industrial) | Engineered (longer) | Low (reputable DE) | High - cabinet weight >500 kg; cost | Fail
EA Elektro-Automatik PSI 10000 | ~EUR 120k-170k for ~250 kW (multi-chassis) | Catalogue (weeks) | Very low (top-tier EU/US) | High - air cooled, not mobile-rated, very costly to scale | Fail
Regatron TopCon TC.P | High (lab-grade, multi-unit) | Catalogue (weeks) | Very low (reputable CH) | High - efficiency/cost; heavy per kW | Fail
Delta Elektronika SM15K | ~EUR 200k+ for ~250 kW (multi-unit) | Catalogue | Very low (top-tier NL) | High - air cooled, cost/kW | Fail
Magna-Power MS/MT series | High (multi-unit) | Catalogue | Very low (reputable US) | High - air cooled, modest efficiency | Fail
Kempower Power Unit + LC Satellite | >EUR 30k complete | Catalogue (weeks-months) | Very low (reputable FI) | Very high - standalone EV charger, not embeddable | Fail

## 5. Final Ranking
Final Ranking - Weighted Scoring Model
Weights: Mandatory compliance 40% ¦ Technical fit 25% ¦ Cost fit 15% ¦ Efficiency & thermal 10% ¦ Comms & integration 5% ¦ Supplier maturity & docs 5%.
Rank | Product | Mandatory 40% | Tech fit 25% | Cost fit 15% | Eff/thermal 10% | Comms 5% | Supplier 5% | OVERALL (0-100)
1 | Infypower LCG1K0135G | 90.6 | 92 | 90 | 85 | 60 | 80 | 88.2
2 | UUGreenPower UR100040-LQ-DD | 90.6 | 90 | 90 | 88 | 60 | 78 | 87.9
3 | MIDA EV Power U3T-A040B-S | 90.6 | 85 | 88 | 78 | 60 | 68 | 84.9
4 | Winline LCR100040A | 87.5 | 85 | 88 | 75 | 60 | 78 | 83.9
5 | Huawei HiCharger 40kW LC module | 87.5 | 85 | 70 | 80 | 60 | 85 | 82
6 | Friem HPB High Power Battery Charger | 78.1 | 78 | 45 | 70 | 90 | 85 | 73.2
7 | Heinzinger ERS | 71.9 | 70 | 30 | 75 | 75 | 85 | 66.3
8 | EA Elektro-Automatik PSI 10000 | 62.5 | 55 | 35 | 78 | 100 | 95 | 61.5
9 | Regatron TopCon TC.P | 62.5 | 62 | 35 | 62 | 85 | 88 | 60.6
10 | Delta Elektronika SM15K | 59.4 | 58 | 38 | 62 | 95 | 92 | 59.5
11 | Magna-Power MS/MT series | 59.4 | 50 | 38 | 55 | 90 | 85 | 56.2
12 | Kempower Power Unit + LC Satellite | 65.6 | 40 | 25 | 80 | 65 | 90 | 55.7
Weighting model
| Mandatory criteria compliance | 40%
| Technical fit for e-PU10 | 25%
| Cost fit (<EUR 20,000 target) | 15%
| Efficiency & thermal performance | 10%
| Communication & integration | 5%
| Supplier maturity & documentation | 5%