e-PU10 400A AC/DC Charger

Project plan

| VDL order number |  |
| --- | --- |
| Customer | Internal |
| End User | Internal – e-PU10 product line |
| Item | 400A AC/DC Charger for e-PU10 BESS |
| Project Lead | L. Rietkerk |
| Kickoff | 23-06-2026 |
| Target completion | 02-11-2026 |

# Introduction

This document defines the scope, deliverables and acceptance criteria for the development of a series-production-ready 400A AC/DC charger option for the e-PU10 BESS. The charger provides a galvanically isolated AC/DC path for the e-PU10 main battery (600–800 VDC) via a single 400A Powerlock set, driven by client demand for higher charging power. The product deadline is November 2026 to align with the e-PU10V2 launch. Execution follows the VDL TRL-based model, tailored to the limited duration of this development.

## Abbreviations

| Abbr. | Definition |
| --- | --- |
| AC / DC | Alternating / Direct Current |
| BESS | Battery Energy Storage System |
| CE | Conformité Européenne |
| EMC | Electromagnetic Compatibility |
| PE | Protective Earth |
| PFC | Power Factor Correction |
| TRL | Technology Readiness Level |

## Objectives

•  Develop a 400A AC/DC charger with galvanic isolation, ready for series production in the e-PU10

•  Liquid cooled, industrial EMC compliant (IEC 61000) design fitting the e-PU10 power module envelope

•  Compliance with CE, IEC 61439, NEN 1010 and other applicable EU standards

•  Continuous operation at 100% rated power under nominal conditions (25 °C)

•  Material cost < 20 000 € per system

•  Integration with e-PU10 controls via ModbusTCP (preferred), CAN, Profinet or EtherCAT

•  Release of series-ready product, documentation and sales material before November 2026

## Deliverables

•  Validated 400A AC/DC charger prototype

•  Mechanical and electrical detailed design package

•  Build book and assembly instructions

•  CE technical file (manual, design calculations, operating instructions)

•  e-PU10 software integration package

•  Test and validation report

•  Sales one-pager and transfer to the sales matrix

# Project Scope

The project covers specification, conceptual and detailed design prototype build validation and series production release of the charger as a module inside the standard e-PU10 power module dimensions. Existing mechanical, thermal and control interfaces are reused. The charger is unidirectional (AC→DC), liquid cooled, galvanically isolated, supports a DC range of at least 600–800 VDC and is controllable down to a minimum of 55 kW / 80 A.

Out of scope: changes to the e-PU10 battery/BMS or cabinet outside the charger envelope, bidirectional operation and field installation/commissioning at customer sites.

## Mandatory (Must-Have) Criteria

•  Galvanic isolation between AC and DC

•  400 / 500 A AC input [Powerlock set (3P + PE)]

•  Unidirectional AC → DC, liquid cooled

•  DC voltage range ~ 600–800 VDC (wider acceptable)

•  Material cost < € 20 000  per system

•  Comms: ModbusTCP (preferred), CAN, Profinet or EtherCAT

•  EU compliant: CE, IEC 61439, NEN 1010 and other applicable standards

•  Mobile-capable, vibration resistant

•  Minimum settable power ≤ 55 kW / 80 A

•  Acceptable inrush with C-type breaker (C80)

•  Fits e-PU10 power module envelope; system weight < 500 kg

•  Heat dissipation < 7 kW (efficiency > 97.5%)

•  DC leakage current < e-PU10 battery precharge capacity

•  Industrial EMC (IEC 61000) or better

## Recommended (Nice-to-Have) Criteria

•  Modular setup in steps of 30–100 kW

•  Hot-swappable / serviceable without interrupting the BESS microgrid

•  High intrinsic reliability (> 98% uptime) through redundancy

•  Active PFC power supply

•  Lower minimum settable power: ≤ 20 kW / 32 A

•  Acceptable inrush with B-type breaker (B32)

## System Requirements

| Parameter | Target |
| --- | --- |
| AC input | 400 A |
| DC output range | 600–800 VDC (wider acceptable) |
| Topology | Unidirectional AC→DC, galvanically isolated |
| Min. settable power | ≤ 55 kW / 80 A (target ≤ 20 kW / 32 A) |
| Efficiency / heat | > 97.5% / < 7 kW |
| Cooling | Liquid cooled |
| Communication | ModbusTCP (pref.), CAN, Profinet, EtherCAT |
| EMC | IEC 61000 industrial or better |
| Envelope / weight | < 500 kg |
| Material cost | < € 20 000 per system |
| Compliance | CE, IEC 61439, NEN 1010 |
| Reliability target | > 98% uptime per system |

# Activities

Execution follows the VDL TRL model, with early phases merged given the compact scope. Each TRL phase ends with a formal tollgate review.

•  TRL 2 – Scope & market research: scope, key results, technical spec, risk and scope-change analysis; supplier/component research (price, quality, documentation)

•  TRL 3 – Conceptual design: component selection, single-line and mechanical concept, cost and engineering-impact estimate, material price estimation

•  TRL 4/5 – Detailed design: mechanical, electrical, e-PU10 software integration, CE documentation, build book

•  TRL 6 – Prototype build & test: assembly, functional and performance validation against must-have criteria

•  TRL 8 – Sales readiness: one-pager and technical datasheet

•  TRL 9 – Product release: finalize documentation, transfer to sales matrix

## Progress review

•  Weekly project update meeting (technical alignment, planning, actions)

•  Bi-weekly engineering management progress review

•  Formal TRL tollgate review per phase, using the standard tollgate template

•  Continuous task and planning tracking in GitHub

•  Standard reporting: technical progress, open actions/risks, budget and hours, roadblocks

Project information is stored in VDL OneDrive during execution at location AC-DC Charger - 400A - 275kW

Controlled documents (design files, 3D models, CE file) migrate to PDM / G drive on release.

# Planning and Milestones

Total effort ≈ 320 h gross / 260 h net across a small multi-disciplinary team.

| Milestone | TRL | Estimated Hours |
| --- | --- | --- |
| Kickoff |  |  |
| Scope frozen & market research complete | TRL 2 | 32 |
| Conceptual design approved | TRL 3 | 26 |
| Detailed design complete (mech/elec/sw/doc) | TRL 4/5 | 180 |
| Prototype built and tested | TRL 6 | 56 |
| Sales material ready | TRL 8 | 8 |
| Product released, transferred to sales matrix | TRL 9 | 8 |

# Risk Management

Key risks:

•  Availability of suitable 400A isolated AC/DC modules within the cost target

•  Thermal performance within the e-PU10 envelope (< 7 kW, > 97.5% efficiency)

•  EMC compliance under industrial conditions (IEC 61000)

•  Inrush compatibility with C-type (and ideally B-type) breakers

•  Integration and communication reliability with the e-PU10 controls

•  Dependency on the e-PU10V2 development timeline

•  Supplier lead times for power electronics and Powerlock connectors

•  CE / IEC 61439 / NEN 1010 documentation completeness

Mitigation: early supplier engagement in TRL 2; conservative thermal/EMC margins in concept; incremental TRL validation with formal tollgates; continuous alignment with the e-PU10V2 team; progressive compliance verification during detailed design.

# Cost, Budget and Team

•  Material cost target: < 20 000 € per system

- Including

  - AC/DC charger module(s) (hardware and software)

  - All required internal power and communication cabling

  - Complete 400 A Powerlock connector set

  - Mechanical rack, mounting structure, and associated hardware

•  Engineering effort: 260 net / 320 gross hours

Required disciplines:

| Discipline | Person |
| --- | --- |
| Project Lead | Lennard Rietkerk |
| Electrical | Szablocs Mozer |
| Mechanical | Bernd Klink |
| Software | Tim Kers / Robert Visscher |
| Safety/Compliance (CE, IEC 61439, NEN 1010), | Gertjan Eegdeman |
| Test & Validation. | Daria Dudareva / Tim Kers |

Prerequisites:

- Approved project number and budget

- e-PU10 (V2) test platform available

- GitHub project and planning established

- PLM/document control structure defined

- Engineering team and roles assigned

# Departments and Communication

- Engineering:

  - Electrical and mechanical design

  - e-PU10 software integration

  - Test specification and execution

  - Supplier coordination

  - Documentation

- Quality

  - CE technical file

  - IEC 61439 / NEN 1010 compliance verification

  - Safety assessment

- Operations & Procurement

  - Sourcing of power electronics

  - Powerlock and cooling components

  - Supplier and lead-time management

  - Prototype assembly and workshop support

  - Series production transfer

Communication:

Daily informal alignment / Weekly project update meeting / bi-weekly management review / formal tollgate review per TRL / actions tracked in GitHub.

# Acceptance Criteria

•  CE certified and compliant with IEC 61439 and NEN 1010

•  Fail-safe and reliable with redundancy where applicable

•  100% rated power continuously available at 25 °C (not a showstopper)

•  Easy to maintain (hot-swappable as nice-to-have)

•  All mandatory technical specifications validated by test

•  Complete documentation set released (build book, CE file, manuals, sales one-pager)

# Dependencies and Assumptions

Dependencies:

•  e-PU10V2 development (mechanical envelope, control and thermal interfaces)

•  Availability of an e-PU10 test platform during TRL 6

•  Supplier lead times for isolated AC/DC modules and Powerlock connectors

Assumptions:

•  e-PU10V2 mechanical and control interfaces frozen before TRL 4/5

•  Suitable 400A isolated AC/DC modules available within cost target

•  Existing e-PU10 liquid cooling capacity sufficient for the additional heat load

•  Engineering capacity available across all required disciplines per plan

# Tollgate Review and Accreditation

Each TRL phase ends with a formal tollgate review of technical maturity, requirement compliance and readiness to proceed, based on objective evidence (test results, design documentation, subsystem validation).

Assessment criteria: completion of TRL-specific deliverables; verification of key system functions for the phase; resolution of critical issues from the previous phase; completion of required tests and documentation updates.

Outcomes: Approved (proceed); Approved with actions (proceed with tracked non-blocking items); Not approved (additional work required).