## Diagnostic Alarm Overview

Severity:

- 0: None

- 1: Info

- 2: Warning

- 3: Normal Shutdown

- 4: Quick Shutdown

- 5: Emergency Shutdown

### 1. Enclosure Climate

| ID | Alarm Message | Trigger Condition | Sever | Auto Clear | Ack Access | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Humidity high | get.events.b_HumidityHigh | 2 | Yes | - | Check enclosure humidity sensor value, ventilation, condensation risk, environmental conditions, and cooling/dehumidification system operation. |
| 2 | Humidity too high | get.events.b_HumidityTooHigh | 4 | No | Operator | Critical humidity level detected. Check water ingress, cooling system failure, humidity sensor calibration, and risk of condensation on electrical components. |
| 3 | Temperature high | get.events.b_TemperatureHigh | 2 | Yes | - | Check enclosure temperature trend, ambient temperature, airflow, fans, filters, and thermal load. |
| 4 | Temperature too high | get.events.b_TemperatureTooHigh | 4 | No | Operator | Critical overtemperature condition. Check cooling failure, blocked airflow, fan status, ambient conditions, and temperature sensor accuracy. |
| 5 | Temperature low | get.events.b_TemperatureLow | 2 | Yes | - | Check heater operation, ambient temperature, enclosure insulation, and temperature sensor readings. |
| 6 | Temperature too low | get.events.b_TemperatureTooLow | 3 | No | Operator | Temperature below operational limit. Check heating system, environmental conditions, and sensor validity. |
| 7 | Analog input temp/humid overrange | get.events.b_AIOverrange | 2 | Yes | - | Analog measurement exceeds sensor range. Check sensor wiring, scaling, and input module configuration. |
| 8 | Analog input temp/humid underrange | get.events.b_AIUnderrange | 2 | Yes | - | Analog measurement below valid range. Check sensor connection, broken cable, and input configuration. |
| 9 | Analog input temp/humid error | get.events.b_AIError | 2 | Yes | - | Analog input hardware error. Check IO module diagnostics and sensor connection. |
| 10 | Dewpoint too high alarm | get.events.b_DewpointTooHigh | 3 | - | - | High dewpoint condition. Check humidity level, temperature difference, condensation risk, and enclosure climate control. |

# 2. Enclosure Doors

| ID | Alarm Message | Trigger Condition | Sever | Auto Clear | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- |
| 1 | Client panel opened | NOT(get.b_ClientpanelDoorClosed) | 1 | Yes | Check client panel door position switch and physical door status. Verify switch alignment and wiring. |
| 2 | Control panel opened | NOT(get.b_ControlPanelDoorClosed) | 1 | Yes | Check control panel door switch, mechanical alignment, and safety circuit wiring. |

# 3. Enclosure LED

| ID | Alarm Message | Trigger Condition | Sever | Auto Clear | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- |
| 1 | LED error | get.b_error | 1 | Yes | Check LED module status, supply voltage, communication wiring, and LED controller diagnostics. |

# 4. Generator Communication

| ID | Alarm Message | Trigger Condition | Sever | Troubleshooting Information |
| --- | --- | --- | --- | --- |
| 1 | Communication not ok | NOT get.CommunicationOK AND set.enable AND st_params.GenControlProtocol <> 0 | 1 | Check generator communication interface, protocol settings, network wiring, and genset controller status. |
| 2 | Fuel at low level / critically low fuel level | get.FuelLow OR get.FuelCritical | 1 | Check fuel sensor value, fuel level, sensor wiring, and generator fuel supply. |

# 5. Harting IO

| Error ID | Alarm Message | Trigger Condition | Sever | Troubleshooting Information |
| --- | --- | --- | --- | --- |
| 1 | External shutdown triggered | get.b_ExtSystemShutdownRequest | 3 | Check external shutdown source, external controller, IO wiring, and emergency shutdown chain. |
| 2 | External EMstop triggered | (PrimaryInputContactSignal = EMSTOP OR SecondaryInputContactSignal = EMSTOP) AND NOT get.b_ExtEMstopOK | 4 | Check external emergency stop devices, safety relay status, wiring continuity, and reset conditions. |

# 6. Internal Power Supply

| ID | Alarm Message | Trigger Condition | Sever | Auto Clear | Trigger Delay | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | AC PSU fault | Get.Events.b_ACPSUFault | 2 | Yes | 3 s | Check AC PSU input voltage, PSU status LEDs, mains supply, wiring, and PSU output voltage. |
| 2 | DC PSU fault | Get.Events.b_DCPSUFault | 2 | Yes | 3 s | Check DC PSU output voltage, DC distribution, overload conditions, and PSU diagnostics. |
| 3 | 24V supply failed | b_DCPSUFault AND b_ACPSUFault | 4 | - | - | Check complete 24V supply chain, AC input, PSU modules, fuses, and DC load. |
| 4 | CEE standby power input fuse error | b_CEEInputFuseTripped | 2 | Yes | - | Check standby power input fuse, CEE connection, and input circuit protection. |
| 5 | Internal supply Grid fuse error | b_GridInputFuseTripped | 4 | - | - | Check internal grid supply fuse, short circuit conditions, and upstream protection. |
| 6 | HVDC shutdown sequence failed | b_HVDCShutdownTimeExceeded | 4 | - | - | Check HVDC discharge circuit, contactors, feedback signals, and shutdown sequence timing. |
| 8 | System shut down in: remaining time | UPS.Get.Events.b_BatteryLowWarning | 2 | Yes | - | Check UPS battery capacity, charging system, battery health, and estimated shutdown timer. |
| 9 | Shutdown initiated: Halt system operation | LowBatShutdownTimer.Q | 4 | Yes | - | UPS battery shutdown sequence active. Check battery status and external power availability. |

# 7. UPS

| ID | Alarm Message | Trigger Condition | Sever | Auto Clear | Trigger Delay | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Low battery error | Get.Events.b_BatteryLowError | 3 | - | 30 s | Check UPS battery voltage, battery age, charging system, and mains availability. |
| 2 | Low battery warning | Get.Events.b_BatteryLowWarning | 2 | Yes | 1 s | Battery capacity reduced. Check UPS load, charging status, and battery condition. |
| 3 | UPS input undervoltage | Get.Events.b_InputVoltageWarning | 2 | Yes | - | Check UPS input supply voltage and upstream power source. |
| 4 | No battery error | Get.Events.b_NoBatteryError | 2 | - | 5 s | Check battery connection, battery presence detection, wiring, and battery breaker/fuse. |

## 8. Neutral Transformer

| ID | Alarm Message | Trigger Condition | Sever | Auto Clear | Trigger Delay | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | High temperature L1 warning | b_TemperatureHighPhase[L1] | 2 | Yes | - | Check L1 temperature sensor, transformer loading, cooling airflow, and sensor wiring. |
| 2 | High temperature L2 warning | b_TemperatureHighPhase[L2] | 2 | Yes | - | Check L2 temperature sensor, transformer loading, cooling airflow, and sensor wiring. |
| 3 | High temperature L3 warning | b_TemperatureHighPhase[L3] | 2 | Yes | - | Check L3 temperature sensor, transformer loading, cooling airflow, and sensor wiring. |
| 4 | High temperature L1 alarm | b_TemperatureTooHighPhase[L1] | 3 | No | Configurable * | Critical L1 overheating. Check phase load imbalance, transformer cooling, ventilation, and temperature measurement. |
| 5 | High temperature L2 alarm | b_TemperatureTooHighPhase[L2] | 3 | No | Configurable * | Critical L2 overheating. Check phase load imbalance, transformer cooling, ventilation, and temperature measurement. |
| 6 | High temperature L3 alarm | b_TemperatureTooHighPhase[L3] | 3 | No | Configurable * | Critical L3 overheating. Check phase load imbalance, transformer cooling, ventilation, and temperature measurement. |
| 7 | Voltage unbalance fault | b_VoltageUnbalanceTooHigh | 3 | No | Configurable** | Check phase voltages, grid quality, transformer connection, and load distribution. |
| 8 | Voltage unbalance warning | b_VoltageUnbalanceHigh | 2 | Yes | - | Monitor phase voltage deviation and investigate increasing imbalance. |
| 9 | Neutral current too high alarm | b_NeutralCurrentTooHigh | 3 | No | 10 s | Check neutral conductor loading, phase imbalance, harmonic currents, and current sensor. |
| 10 | Neutral current high warning | b_NeutralCurrentHigh | 2 | Yes | - | Investigate increasing neutral current, phase imbalance, and nonlinear loads. |
| 11 | OCP warning | b_OvercurrentAlarm | 3 | No | 1 s | Check overcurrent protection settings, load current, and protection trip source. |
| 12 | OCP warning | b_Overcurrentwarning | 2 | Yes | - | Check load current trend and protection margins. |

Configurable*: Configurable temperature trip delay.

Configurable**: Configurable voltage unbalance delay.

# 9. Peakshave Box

| ID | Alarm Message | Trigger Condition | Sever | Auto Clear | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- |
| 1 | Buscoupler not detected | NOT Get.b_buscouplerReady AND b_enable | 2 | Yes | Check bus coupler communication, power supply, wiring, and enable configuration. |
| 2 | L1 error | PowerStatus.b_Error_Phase[1] | 2 | Yes | Check L1 voltage measurement, phase connection, and power monitoring device. |
| 3 | L2 error | PowerStatus.b_Error_Phase[2] | 2 | Yes | Check L2 voltage measurement, phase connection, and power monitoring device. |
| 4 | L3 error | PowerStatus.b_Error_Phase[3] | 2 | Yes | Check L3 voltage measurement, phase connection, and power monitoring device. |
| 6 | Powermonitor current L1 out of range | b_OverCurrent AND Error_Phase[1] | 2 | Yes | Check L1 current sensor and load current. |
| 7 | Powermonitor current L2 out of range | b_OverCurrent AND Error_Phase[2] | 2 | Yes | Check L2 current sensor and load current. |
| 8 | Powermonitor current L3 out of range | b_OverCurrent AND Error_Phase[3] | 2 | Yes | Check L3 current sensor and load current. |
| 9 | Powermonitor general warning | b_GeneralWarning | 2 | Yes | Check power monitor diagnostic register. |
| 11 | Powermonitor overcurrent fault | b_OverCurrent | 2 | Yes | Check load current, CT measurement, and protection limits. |
| 12 | Powermonitor overvoltage fault | b_OverVoltage | 2 | Yes | Check grid voltage and voltage measurement accuracy. |
| 13 | Powermonitor undervoltage fault | b_UnderVoltage | 2 | Yes | Check grid supply, voltage dips, and measurement circuit. |
| 14 | PSB settings change blocked, disable PSB to apply | b_SettingsChangePending | 2 | Yes | Disable Peakshave Box before applying configuration changes. |

# 10. PLC Status

| ID | Alarm Message | Trigger Condition | Sever | Troubleshooting Information |
| --- | --- | --- | --- | --- |
| 1 | EL9410 supply fault | EL9410.bit_UpUndervoltage OR EL9410.bit_UsUndervoltage | 4 | Check PLC IO supply voltage, 24V supply, wiring, and EL9410 module diagnostics. |
| 2 | EtherCAT master fault | events.b_EthercatMasterFault | 3 | Check EtherCAT network, slave devices, cables, and PLC communication status. |

# 11. Power Quality Monitor (Janitza / EL3443)

| ID | Alarm Message | Trigger Condition | Sever | Trigger Delay | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- |
| 1 | Janitza communication warning | b_MBCommWarning | 2 | - | Check Modbus communication, address configuration, cable connection, and device status. |
| 2 | Janitza communication timeout | b_MBTimeoutWarning | 2 | - | Check communication timeout settings, network load, and Modbus master status. |
| 3 | Janitza communication fault | b_MBCommError | 3 | 10 s | Check Janitza power meter availability, communication wiring, and Modbus configuration. |
| 4 | EL3443 power monitor warning | b_EL3443Warning | 2 | - | Check EL3443 module diagnostics and measurement values. |

# 12. Power Module (POWERSTACK)

| ID | Alarm Message | Trigger Condition | Sever | Auto Clear | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- |
| 1 | DC voltage difference between powermodules high | Get.Events.b_DCdeviationHigh | 2 | No | Check DC link voltage measurement, power module balancing, module communication, and DC connection quality. |
| 2 | Temperature difference between powermodules high | Get.Events.b_TemperatureDeviationHigh | 2 | Yes | Check cooling distribution, module temperature sensors, airflow, and thermal loading differences. |
| 3 | Under frequency trip | Get.Events.b_UnderFreqFault | 3 | No | Check grid frequency, grid connection, frequency protection settings, and grid quality. |
| 4 | Over frequency trip | Get.Events.b_OverFreqFault | 3 | No | Check grid frequency, grid stability, frequency protection settings, and external grid conditions. |
| 5 | Cooling system derating causing inverter output to be limited | Get.Events.b_CoolingDerating | 2 | Yes | Check cooling system operation, pumps/fans, coolant temperature, flow rate, and filters. |
| 6 | SFC error at step | SFCerror | 3 | No | Check startup sequence step, inverter state machine, communication, and failed transition condition. |
| 8 | Inverter starting in grid following mode inhibited | NOT get.b_StartEnabled AND Mode=Afe | 1 | Yes | Check grid code status, AC availability, and inverter start permission conditions. |
| 9 | Inverter starting in grid forming mode inhibited | NOT get.b_StartEnabled AND Mode=Island | 1 | Yes | Check AC bus condition and island mode startup requirements. |
| 10 | Overvoltage fault | get.Events.b_OverVoltageFault | 2 | No | Check DC/AC voltage measurement, grid voltage, inverter voltage control, and protection settings. |
| 11 | Undervoltage fault | get.Events.b_underVoltageFault | 2 | No | Check DC bus voltage, grid voltage, supply stability, and voltage sensing. |
| 12 | Overvoltage warning | get.Events.b_OverVoltageFault | 2 | Yes | Verify if warning trigger is intentionally shared with overvoltage fault. Check voltage trend. |
| 13 | Undervoltage warning | get.Events.b_underVoltageFault | 2 | Yes | Verify if warning trigger is intentionally shared with undervoltage fault. |
| 14 | Temperature fault | get.Events.b_TemperatureFault | 2 | Yes | Check inverter temperature sensors, cooling, and thermal protection. |
| 15 | Temperature warning | get.Events.b_TemperatureWarning | 2 | Yes | Check temperature increase trend and cooling performance. |
| 16 | Power limit reached, shutdown in remaining time | b_PlimitShutdownWarning | 2 | Yes | Check inverter power limitation cause, temperature, grid restrictions, and remaining shutdown timer. |
| 17 | Power limit shutdown | b_PlimitShutdown | 3 | Yes | Check why inverter power limit protection reached shutdown threshold. |
| 18 | Power limiting mode active, output on hold | b_PlimitShiftingActive | 2 | Yes | Check power limitation mode, grid restrictions, and system control settings. |
| 19 | Gridcode disconnect active | b_GridCodeWarning | 2 | Yes | Check grid code requirements, reconnection timer, grid availability, and grid quality. |

# 13. Fire Detection

| ID | Alarm Message | Trigger Condition | Sever | Auto Clear | Trigger Delay | Ack Access | SMS / VDL | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Alarm muted | events.AlarmMuted | 1 | Yes | - | General | - | Check fire panel status and whether alarm was intentionally muted. |
| 2 | Smoke detector not OK | SmokeDetFault | 2 | Yes | 5 s | Operator | - | Check smoke detector communication, power supply, sensor contamination, and wiring. |
| 3 | Smoke detector alarm | SmokeDetAlarm | 4 | No | - | VDL | Yes | Check smoke detector location, fire indication, and verify with physical inspection. |
| 4 | CO detector not OK | CODetFault | 2 | Yes | 2 s | Operator | - | Check CO detector supply, communication, calibration, and sensor status. |
| 5 | CO Detector warning level 1 | CODetWarning1 | 1 | Yes | - | Operator | No | Check CO concentration trend and ventilation conditions. |
| 6 | CO Detector warning level 2 | CODetWarning2 | 2 | Yes | - | Operator | No | Check increasing CO level and investigate possible source. |
| 7 | CO Detector alarm level | CODetAlarm | 3 | - | - | VDL | Yes | Check CO concentration, ventilation failure, and possible combustion source. |

# 14. Insulation Monitor

| ID | Alarm Message | Trigger Condition | Sever | Auto Clear | Ack Access | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Disabled | NOT get.b_Enabled | 1 | Yes | - | Verify insulation monitor enable configuration. |
| 2 | Warning level | get.b_warning | 2 | No | Operator | Check insulation resistance value, leakage current, and connected loads. |
| 3 | PEN link detected | get.b_PENlinkDetected | 1 | Yes | Operator | Check PEN link status and earthing configuration. |
| 4 | PEN link not detected in TN earthing system | b_PENlinkdiscrepance | 3 | No | Operator | Check PEN connection, earthing system configuration, and switching device. |
| 5 | PEN link switched during operation | get.b_PENlinkOperatedFault | 2 | No | Operator | Check PEN switching operation and prevent switching under load. |
| 6 | Configured earthing system not corresponding to PENlink state | get.b_EarthingSystemMismatch | 3 | No | Operator | Check configured earthing mode versus actual hardware state. |
| 7 | No earthing system selected, starting not allowed | get.b_NoEarthingSystemSet | 2 | Yes | - | Configure correct earthing system before startup. |

# 15. Over Current Protection (OCP)

| ID Range | Alarm Group | Trigger Condition | Sever | Troubleshooting Information |
| --- | --- | --- | --- | --- |
| 1-16 | Input overcurrent warnings and alarms | Get.Events.Input[i][phase].b_warning / b_alarm | 2 | Check input currents, phase loading, neutral current, current sensors, and protection settings. |
| 17-40 | Output overcurrent warnings and alarms | Get.Events.Output[i][phase].b_warning / b_alarm | 2 / 3 | Check output loads, MCCB status, current measurement, and overload duration. |
| 41 | Output MCCB trip | Get.b_OutputAlarm | 2 | Check MCCB trip status, peak current, duration, and affected phase location. |

# 16. Residual Current Monitor (RCM)

| ID | Alarm Message | Trigger Condition | Sever | Auto Clear | Ack Access | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | RCD prewarning | Disabled (FALSE) | 2 | Yes | General | Obsolete alarm. Verify if RCM prewarning functionality is still required. |

# 17. Surge Protection

| ID | Alarm Message | Trigger Condition | Sever | Ack Access | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- |
| 1 | Type 1+2 Fault | NOT get.b_Type12_OK | 2 | VDL | Check surge protection module status indicators and replace damaged protection cartridge if required. |
| 2 | Type 3 Fault | NOT get.b_Type3_OK | 2 | VDL | Check Type 3 surge protection device and replacement indication. |

# 18. Safety System

| ID | Alarm Message | Trigger Condition | Sever | SMS / VDL | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- |
| 1 | Emergency stop channel A | NOT get.b_EStopChannelAOK | 5 | Yes | Check emergency stop circuit channel A, safety relay, wiring, and contacts. |
| 2 | Emergency stop channel B | NOT get.b_EStopChannelBOK | 5 | No | Check emergency stop circuit channel B and redundancy monitoring. |
| 3 | Residual current fault detected | NOT get.b_MRCDBOK | 5 | Yes | Check RCD/MRCDB device, leakage current, and safety circuit. |
| 4 | Insulation fault detected | NOT get.b_InsulationMonitorOK | 5 | Yes | Check insulation resistance and insulation monitoring system. |
| 5 | Inverter door opened | NOT get.b_InverterDoorOK | 5 | Yes | Check inverter door switches and mechanical locking. |
| 6 | ZPT overcurrent trip | NOT get.b_ZptOK | 5 | Yes | Check ZPT protection device and overcurrent event. |
| 10 | Emergency stop initiated | NOT get.b_SafetyOK | 5 | No | Check complete safety chain and active safety device. |

# 19. System Control

| ID | Alarm Message | Trigger Condition | Sever | Auto Clear | Ack Access | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Machine name update pending in VDL Powernet: System restart required | b_RestartRequiredMachineName | 1 | - | - | Restart system after machine name update to apply configuration. |
| 2 | External IO initiated system shutdown | HartingIO.b_ExtSystemShutdownRequest | 3 | No | - | Check external shutdown request source and IO wiring. |
| 3 | System time update failed | b_TimeUpdateFailed | 1 | Yes | General | Check NTP/time synchronization settings, network connection, and time server availability. |

# 20. AC DC Charger

| ID | Alarm Message | Trigger Condition | Sever | Trigger Delay | Troubleshooting Information |
| --- | --- | --- | --- | --- | --- |
| 1 | Buscoupler not found | st_params.b_ACDCChargerFitted | 2 | 2 s | Check buscoupler and its connection |
| 2 | Input phase missing | get.Events.B_ACPhaselossFault | 2 | 1 s | Check AC connection, fuse or connector |
| 3 | Input Overvoltage detected | get.Events.B_ACOvervoltage | 2 | 1 s | Check input voltage and voltage measurement accuracy. Check trends. |
| 4 | Input Undervoltage detected | get.Events.B_ACUndervoltage | 2 | 1 s | Check input voltage and voltage measurement accuracy. Check trends. |
| 5 | Charger failed to generate output | get.Events.b_FailedToGenerateDCOutput | 2 | 1 s | Check each module and its DC voltage output |